## GCF CALC ACTIVE SHEET
|  |  |  | © Jemena Gas Networks (NSW) Ltd. | [6 empty] | DISCLAIMER : Jemena does not warrant that the data in this calculator is correct and it should be used only as a guide for the designer for the design of gas centralised hot water. To obtain the latest version of this model please refer to www.Jemena.net.au or contact your Customer Service Representative - Jemena. Copyright JJemena Gas Networks (NSW) Ltd 2007
ADG-003B - DESIGN GUIDE - MODEL FOR ESTIMATION OF COMMON FACTOR FOR GAS CENTRALISED HOT WATER SYSTEMS (GCHWS) (ISSUE 4 - 22/08/2007) | [10 empty] | \
Note [1] : All cells with white backgrounds are unlocked and require designer input. All other cells are locked and cannot be changed.
| DATE - |  |  | 2007-05-26
| ADDRESS - | [10 empty] | For explanation of this model refer section 5. in "Design Guide for Gas Centralised Hot Water Systems" (Jemena DOCUMENT ADG-003)
| NUMBER OF APARTMENTS - |  |  | 40
SPECIFY PROPOSED BOILER PLANT HERE -
| GCHW THERMAL EFFICIENCY |  |  | 80%
| BOILER MAINTENANCE RATE (MJ/DAY) |  |  | 19.6
| TEMPERATURE RISE (OC) |  |  | 50
[A] HOT WATER AND ENERGY DEMAND SECTION
Table A.1 - Calculation of Number of Points from Inputted Apartment Details
| APARTMENT DWELLINGS | KITCHEN | BATH ROOM | LAUNDRY | EN-SUITE | DISH WASHER | NO. OF BEDROOMS | SUM OF POINTS / UNIT | NO OF UNITS | SUM OF POINTS
| 10 | 1 | 1 | 1 | 0 | 1 | 1 | 5 | 10 | 50 | 1. | Enter individual dwelling data in table A.1 . Refer Appendix -A1 in "Design Guide for Gas Centralised Hot Water Systems" (Jemena DOCUMENT ADG-003)
| 20 | 1 | 1 | 1 | 1 | 1 | 2 | 7 | 20 | 140
| 10 | 1 | 1 | 1 | 1 | 1 | 3 | 8 | 10 | 80
| 0 | 0 | 0 | 0 | 0 | 0 | 5 | 5 | 0 | 0
| 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[8 empty] | TOTAL NO. OF POINTS= |  | 270
Table A.2 Calculated Nominal Hot Water Flow (at 65deg.C Before Mixing With Cold Water) and Equivalent Energy Content
| TOTAL NO. OF POINTS | CALCULATED COINCIDENCE FACTOR | HOT WATER POINT DELIVERY (lit./min/point) | MAX. WATER DELIVERY FROM BOILER (lit/min) | AVERAGE HOT WATER SUPPLY FROM HOURLY RECOVERY RATE FROM GCHWS (lit/hr) | SPECIFY DAILY HOT WATER DEMAND PER APARTMENT (lit/apart./day) | CALCULATED DAILY HOT WATER (65OC) DEMAND (lit/day) | ENERGY REQUIRED TO HEAT 1.0 LITRE WATER TO TEMP (MJ/lit) | GAS ENERGY INPUTED TO BOILER FOR WATER CONSUMED (MJ/day) |  | 2. | Observe calculated design flowrates in table A.2 based table A.1. values . Observe energy consumption for hot water use based on 110 lit/apartment/day
| 270 | 0.166 | 4.56 | 204.3792 | 3065.688 | 110 | 4400 | 0.26169 | 1151.425
[B] HEAT LOSS AND GAIN SECTION
| Table B.1 PIPEWORK HEAT LOSSES | [7 empty] | Table B.2 OTHER HEAT LOSSES
| PIPE SIZE | INSULATION THICKNESS (mm) | " 65 O.C HOT WATER / 15 deg.C AMBIENT with Thermotec 4 zero insulation" ) | " 50 O.C TEMPERED WATER System/ 15deg.C AMBIENT with ARMAFLEX insulation" ) | INPUT LENGTH OF PIPE HERE | UNIT HEAT LOSS FOR COLUMN <F> | UNIT HEAT LOSS FOR COLUMN <G> |  | HW METER LOSS @ 0.1MJ/hr PER Meter (MJ/day) | 98.4 | 3. | Obtain thermal insulation data from thermal insulation supplier for hot water and ambient conditions shown . Inputted values to be in units of, "kJ/H/m". Input into tabe B.1
| (mm OD) | <Nominate insulation type here> | (kJ/H/m) | (kJ/H/m) | (m) | (kJ/H) | (kJ/H) |  | BOILER MAINTENANCE RATE (MJ/day) | 19.6 | 4. | Insert standing heat loss from individual water meters. Obtain standing heat losses for boiler from manufacturer. Input into tabe B.2
| 15 | nil | 112.3 | 50.4 | 0 | 0 | 0
| 15 | 20 | 31.7 | 19.1 | 23 | 729.1 | 439.3
| 15 | 25 | 25.2 | 16.9 | 95 | 2394 | 1605.5
| 20 | nil | 144.7 | 78.5 | 0 | 0 | 0
| 20 | 20 | 36.6 | 25.9 | 0 | 0 | 0
| 20 | 25 | 31.3 | 22.7 | 295 | 9233.5 | 6696.5
| 25 | nil | 177.1 | 97.9 | 0 | 0 | 0
| 25 | 20 | 40.3 | 28.4 | 0 | 0 | 0
| 25 | 25 | 37.4 | 25.2 | 98 | 3665.2 | 2469.6
| 32 | nil | 218.2 | 124.9 | 0 | 0 | 0
| 32 | 20 | 47.5 | 32.2 | 0 | 0 | 0 |  |  |  | 5. | Input individual pipe size quantities for the central hot water pipe loop into table B.1. Observe the corresponding heat loss rate from specific CHW pipe sizes as a function of ambient temeprature and insulation thicknesses.
| 32 | 25 | 41.8 | 28.1 | 65 | 2717 | 1826.5
| 40 | nil | 258.1 | 149 | 0 | 0 | 0
| 40 | 20 | 58 | 36.4 | 0 | 0 | 0
| 40 | 25 | 50.8 | 31.1 | 18 | 914.4 | 559.8
| 50 | nil | 324.7 | 200.2 | 0 | 0 | 0
| 50 | 20 | 64.1 | 44.6 | 0 | 0 | 0
| 50 | 25 | 58 | 38.5 | 20 | 1160 | 770
| 65 | nil | 372.9 | 262.6 | 0 | 0 | 0
| 65 | 20 | 71.6 | 54.7 | 0 | 0 | 0
| 65 | 25 | 64.4 | 46.4 | 8 | 515.2 | 371.2
| 80 | nil | 439.6 | 313.6 | 0 | 0 | 0
| 80 | 20 | 85.3 | 63 | 0 | 0 | 0
| 80 | 25 | 76.3 | 49.7 | 0 | 0 | 0
| 100 | nil | 590.1 | 398.2 | 0 | 0 | 0
| 100 | 20 | 106.2 | 76.3 | 0 | 0 | 0
| 100 | 25 | 88.9 | 59.2 | 0 | 0 | 0
|  | Total Central Hot Water Piping Heat Loss ( MJ/H) = |  |  |  | 21.3284 | 14.7384
|  | Total Central Hot Water Piping Heat Loss ( MJ/day) = |  |  |  | 511.8816 | 353.7216
Table B.3 ENERGY GAINS FROM AUGMENTATIONS (MJ/day)
|  | SOLAR THERMAL PANELS (MJ/day) |  | define panels and config |  | 0 |  |  |  |  | 6. | Input daily energy contributions from renewable energy augmentations such as,solar-thermal; co-generation; fuel cells; etc.. .
|  | TOTAL ENERGY AUGMENTATION |  |  |  | 0
[C] HEAT CALCULATIONS AND COMMON FACTOR
|  |  | CONSUMED HOT WATER ENERGY (MJ/day) | BOILER MAINTENANCE AND METER/VALVE LOSSES (MJ/day) | LOSSES FROM CHWP MANIFOLD (MJ/day) | HEAT GAINS FROM AUGMENTATION (MJ/day) | TOTAL ENERGY | COMMON FACTOR (MJ/lit) | GENRALISED COMMON FACTOR (kJ/lit/deg.C)
|  | COLUMN <F> INSULATION | 1151.425 | 118 | 511.8816 | 0 | 1781.3066 | 0.40484 | 8.0968 |  | 7. | Observe calculated common factor values and generalised common factor values for two(2) simulated conditions in table C
|  | COLUMN <G> INSULATION | 1151.425 | 118 | 353.7216 | 0 | 1623.1466 | 0.3689 | 7.3779
Note on D14: Based on point methodology and data from "The Raypak Hot Water Manual" (Reproduced with permission of Rheem Australia Pty Ltd)
Note on F25: Designer Input: [Default is 4.56 (lit/min/point)]
Note on F29: Designer State Heat Loss conditions here (eg " 65 deg.C HOT WATER / 15 deg.C AMBIENT" ) Instructions to designer: -Input heat loss data here available from by insulation supplier. For the purpose of this example Thermotec 4 Zero R heat loss data has been provided by Thermotec Foam and NuWave Noise Barrier Products for heat loss conditions associated with 65 deg.C hot water in copper pipe with Thermotec insulation thickness as shown with 15 deg.C surrounding ambient temperature.
Note on F30: UNITS OF HEAT LOSS - To convert Heat Loss in units of W/m into units of, kJ/H/m, - multiply by 3.60
Note on G8: Input all brand and model details e.g.: Rheem 4 x 621 275 @ 800MJ/hr ; 3,861 lit/hr recovery
Note on I25: Designer Input: [Default is 110 (lit/apartment/day)]

## DIVERSITY DATA
Reproduced from "The Raypak Hot Water Manual" with the permission of Rheem Australia Pty Ltd
NUMBER OF POINTS | DIVERSITY FACTOR | FLOW RATE (l/min) | Max. Demand (lit/hr)
1 | 1 | 4.6 | 69
2 | 0.85 | 7.82 | 117.3
3 | 0.76 | 10.488 | 157.32
4 | 0.7 | 12.88 | 193.2
5 | 0.665 | 15.295 | 229.425
6 | 0.645 | 17.802 | 267.03
7 | 0.63 | 20.286 | 304.29
8 | 0.597 | 21.9696 | 329.544
9 | 0.57 | 23.598 | 353.97
10 | 0.545 | 25.07 | 376.05
11 | 0.524 | 26.5144 | 397.716
12 | 0.507 | 27.9864 | 419.796
13 | 0.484 | 28.9432 | 434.148
14 | 0.466 | 30.0104 | 450.156
15 | 0.452 | 31.188 | 467.82
16 | 0.437 | 32.1632 | 482.448
17 | 0.425 | 33.235 | 498.525
18 | 0.412 | 34.1136 | 511.704
19 | 0.4 | 34.96 | 524.4
20 | 0.39 | 35.88 | 538.2
21 | 0.38 | 36.708 | 550.62
22 | 0.372 | 37.6464 | 564.696
23 | 0.363 | 38.4054 | 576.081
24 | 0.354 | 39.0816 | 586.224
25 | 0.345 | 39.675 | 595.125
26 | 0.337 | 40.3052 | 604.578
27 | 0.33 | 40.986 | 614.79
28 | 0.323 | 41.6024 | 624.036
29 | 0.316 | 42.1544 | 632.316
30 | 0.31 | 42.78 | 641.7
31 | 0.305 | 43.493 | 652.395
32 | 0.296 | 43.5712 | 653.568
33 | 0.29 | 44.022 | 660.33
34 | 0.285 | 44.574 | 668.61
35 | 0.28 | 45.08 | 676.2
36 | 0.275 | 45.54 | 683.1
37 | 0.27 | 45.954 | 689.31
38 | 0.266 | 46.4968 | 697.452
39 | 0.26 | 46.644 | 699.66
40 | 0.257 | 47.288 | 709.32
41 | 0.253 | 47.7158 | 715.737
42 | 0.249 | 48.1068 | 721.602
43 | 0.244 | 48.2632 | 723.948
44 | 0.241 | 48.7784 | 731.676
45 | 0.237 | 49.059 | 735.885
46 | 0.234 | 49.5144 | 742.716
47 | 0.231 | 49.9422 | 749.133
48 | 0.228 | 50.3424 | 755.136
49 | 0.225 | 50.715 | 760.725
50 | 0.223 | 51.29 | 769.35
51 | 0.22 | 51.612 | 774.18
52 | 0.218 | 52.1456 | 782.184
53 | 0.216 | 52.6608 | 789.912
54 | 0.214 | 53.1576 | 797.364
55 | 0.212 | 53.636 | 804.54
56 | 0.21 | 54.096 | 811.44
57 | 0.209 | 54.7998 | 821.997
58 | 0.208 | 55.4944 | 832.416
59 | 0.206 | 55.9084 | 838.626
60 | 0.205 | 56.58 | 848.7
61 | 0.204 | 57.2424 | 858.636
62 | 0.2025 | 57.753 | 866.295
63 | 0.202 | 58.5396 | 878.094
64 | 0.2007 | 59.0861 | 886.2912
65 | 0.2005 | 59.9495 | 899.2425
66 | 0.2003 | 60.8111 | 912.1662
67 | 0.2001 | 61.6708 | 925.0623
68 | 0.1998 | 62.4974 | 937.4616
69 | 0.1995 | 63.3213 | 949.8195
70 | 0.1992 | 64.1424 | 962.136
71 | 0.199 | 64.9934 | 974.901
72 | 0.1988 | 65.8426 | 987.6384
73 | 0.1986 | 66.6899 | 1000.3482
74 | 0.1984 | 67.5354 | 1013.0304
75 | 0.1982 | 68.379 | 1025.685
76 | 0.1981 | 69.2558 | 1038.8364
77 | 0.198 | 70.1316 | 1051.974
78 | 0.1978 | 70.9706 | 1064.5596
79 | 0.1976 | 71.8078 | 1077.1176
80 | 0.1974 | 72.6432 | 1089.648
81 | 0.1972 | 73.4767 | 1102.1508
82 | 0.197 | 74.3084 | 1114.626
83 | 0.1966 | 75.0619 | 1125.9282
84 | 0.1962 | 75.8117 | 1137.1752
85 | 0.196 | 76.636 | 1149.54
86 | 0.1956 | 77.3794 | 1160.6904
87 | 0.1953 | 78.1591 | 1172.3859
88 | 0.195 | 78.936 | 1184.04
89 | 0.1946 | 79.6692 | 1195.0386
90 | 0.1942 | 80.3988 | 1205.982
91 | 0.194 | 81.2084 | 1218.126
92 | 0.1936 | 81.9315 | 1228.9728
93 | 0.1932 | 82.651 | 1239.7644
94 | 0.193 | 83.4532 | 1251.798
95 | 0.1926 | 84.1662 | 1262.493
96 | 0.1922 | 84.8755 | 1273.1328
97 | 0.192 | 85.6704 | 1285.056
98 | 0.1916 | 86.3733 | 1295.5992
99 | 0.1912 | 87.0725 | 1306.0872
100 | 0.191 | 87.86 | 1317.9
101 | 0.1905 | 88.5063 | 1327.5945
102 | 0.1902 | 89.2418 | 1338.6276
103 | 0.19 | 90.022 | 1350.33
104 | 0.19 | 90.896 | 1363.44
105 | 0.19 | 91.77 | 1376.55
106 | 0.189 | 92.1564 | 1382.346
107 | 0.189 | 93.0258 | 1395.387
108 | 0.189 | 93.8952 | 1408.428
109 | 0.188 | 94.2632 | 1413.948
110 | 0.187 | 94.622 | 1419.33
111 | 0.187 | 95.4822 | 1432.233
112 | 0.187 | 96.3424 | 1445.136
113 | 0.187 | 97.2026 | 1458.039
114 | 0.186 | 97.5384 | 1463.076
115 | 0.186 | 98.394 | 1475.91
116 | 0.186 | 99.2496 | 1488.744
117 | 0.186 | 100.1052 | 1501.578
118 | 0.185 | 100.418 | 1506.27
119 | 0.185 | 101.269 | 1519.035
120 | 0.185 | 102.12 | 1531.8
121 | 0.184 | 102.4144 | 1536.216
122 | 0.184 | 103.2608 | 1548.912
123 | 0.184 | 104.1072 | 1561.608
124 | 0.183 | 104.3832 | 1565.748
125 | 0.183 | 105.225 | 1578.375
126 | 0.183 | 106.0668 | 1591.002
127 | 0.182 | 106.3244 | 1594.866
128 | 0.182 | 107.1616 | 1607.424
129 | 0.182 | 107.9988 | 1619.982
130 | 0.181 | 108.238 | 1623.57
131 | 0.181 | 109.0706 | 1636.059
132 | 0.181 | 109.9032 | 1648.548
133 | 0.181 | 110.7358 | 1661.037
134 | 0.18 | 110.952 | 1664.28
135 | 0.18 | 111.78 | 1676.7
136 | 0.18 | 112.608 | 1689.12
137 | 0.18 | 113.436 | 1701.54
138 | 0.18 | 114.264 | 1713.96
139 | 0.179 | 114.4526 | 1716.789
140 | 0.179 | 115.276 | 1729.14
141 | 0.179 | 116.0994 | 1741.491
142 | 0.179 | 116.9228 | 1753.842
143 | 0.179 | 117.7462 | 1766.193
144 | 0.178 | 117.9072 | 1768.608
145 | 0.178 | 118.726 | 1780.89
146 | 0.178 | 119.5448 | 1793.172
147 | 0.178 | 120.3636 | 1805.454
148 | 0.178 | 121.1824 | 1817.736
149 | 0.177 | 121.3158 | 1819.737
150 | 0.177 | 122.13 | 1831.95
151 | 0.177 | 122.9442 | 1844.163
152 | 0.177 | 123.7584 | 1856.376
153 | 0.176 | 123.8688 | 1858.032
154 | 0.176 | 124.6784 | 1870.176
155 | 0.176 | 125.488 | 1882.32
156 | 0.176 | 126.2976 | 1894.464
157 | 0.176 | 127.1072 | 1906.608
158 | 0.175 | 127.19 | 1907.85
159 | 0.175 | 127.995 | 1919.925
160 | 0.175 | 128.8 | 1932
161 | 0.175 | 129.605 | 1944.075
162 | 0.175 | 130.41 | 1956.15
163 | 0.174 | 130.4652 | 1956.978
164 | 0.174 | 131.2656 | 1968.984
165 | 0.174 | 132.066 | 1980.99
166 | 0.174 | 132.8664 | 1992.996
167 | 0.174 | 133.6668 | 2005.002
168 | 0.173 | 133.6944 | 2005.416
169 | 0.173 | 134.4902 | 2017.353
170 | 0.173 | 135.286 | 2029.29
171 | 0.173 | 136.0818 | 2041.227
172 | 0.173 | 136.8776 | 2053.164
173 | 0.173 | 137.6734 | 2065.101
174 | 0.173 | 138.4692 | 2077.038
175 | 0.173 | 139.265 | 2088.975
176 | 0.172 | 139.2512 | 2088.768
177 | 0.172 | 140.0424 | 2100.636
178 | 0.172 | 140.8336 | 2112.504
179 | 0.172 | 141.6248 | 2124.372
180 | 0.172 | 142.416 | 2136.24
181 | 0.172 | 143.2072 | 2148.108
182 | 0.172 | 143.9984 | 2159.976
183 | 0.172 | 144.7896 | 2171.844
184 | 0.172 | 145.5808 | 2183.712
185 | 0.172 | 146.372 | 2195.58
186 | 0.172 | 147.1632 | 2207.448
187 | 0.171 | 147.0942 | 2206.413
188 | 0.171 | 147.8808 | 2218.212
189 | 0.171 | 148.6674 | 2230.011
190 | 0.171 | 149.454 | 2241.81
191 | 0.171 | 150.2406 | 2253.609
192 | 0.171 | 151.0272 | 2265.408
193 | 0.171 | 151.8138 | 2277.207
194 | 0.171 | 152.6004 | 2289.006
195 | 0.171 | 153.387 | 2300.805
196 | 0.171 | 154.1736 | 2312.604
197 | 0.171 | 154.9602 | 2324.403
198 | 0.17 | 154.836 | 2322.54
199 | 0.17 | 155.618 | 2334.27
200 | 0.17 | 156.4 | 2346
201 | 0.17 | 157.182 | 2357.73
202 | 0.17 | 157.964 | 2369.46
203 | 0.17 | 158.746 | 2381.19
204 | 0.17 | 159.528 | 2392.92
205 | 0.17 | 160.31 | 2404.65
206 | 0.17 | 161.092 | 2416.38
207 | 0.17 | 161.874 | 2428.11
208 | 0.17 | 162.656 | 2439.84
209 | 0.17 | 163.438 | 2451.57
210 | 0.17 | 164.22 | 2463.3
211 | 0.17 | 165.002 | 2475.03
212 | 0.17 | 165.784 | 2486.76
213 | 0.169 | 165.5862 | 2483.793
214 | 0.169 | 166.3636 | 2495.454
215 | 0.169 | 167.141 | 2507.115
216 | 0.169 | 167.9184 | 2518.776
217 | 0.169 | 168.6958 | 2530.437
218 | 0.169 | 169.4732 | 2542.098
219 | 0.169 | 170.2506 | 2553.759
220 | 0.169 | 171.028 | 2565.42
221 | 0.169 | 171.8054 | 2577.081
222 | 0.169 | 172.5828 | 2588.742
223 | 0.169 | 173.3602 | 2600.403
224 | 0.169 | 174.1376 | 2612.064
225 | 0.169 | 174.915 | 2623.725
226 | 0.169 | 175.6924 | 2635.386
227 | 0.169 | 176.4698 | 2647.047
228 | 0.169 | 177.2472 | 2658.708
229 | 0.169 | 178.0246 | 2670.369
230 | 0.169 | 178.802 | 2682.03
231 | 0.168 | 178.5168 | 2677.752
232 | 0.168 | 179.2896 | 2689.344
233 | 0.168 | 180.0624 | 2700.936
234 | 0.168 | 180.8352 | 2712.528
235 | 0.168 | 181.608 | 2724.12
236 | 0.168 | 182.3808 | 2735.712
237 | 0.168 | 183.1536 | 2747.304
238 | 0.168 | 183.9264 | 2758.896
239 | 0.168 | 184.6992 | 2770.488
240 | 0.168 | 185.472 | 2782.08
241 | 0.168 | 186.2448 | 2793.672
242 | 0.168 | 187.0176 | 2805.264
243 | 0.168 | 187.7904 | 2816.856
244 | 0.168 | 188.5632 | 2828.448
245 | 0.168 | 189.336 | 2840.04
246 | 0.168 | 190.1088 | 2851.632
247 | 0.168 | 190.8816 | 2863.224
248 | 0.168 | 191.6544 | 2874.816
249 | 0.168 | 192.4272 | 2886.408
250 | 0.167 | 192.05 | 2880.75
251 | 0.167 | 192.8182 | 2892.273
252 | 0.167 | 193.5864 | 2903.796
253 | 0.167 | 194.3546 | 2915.319
254 | 0.167 | 195.1228 | 2926.842
255 | 0.167 | 195.891 | 2938.365
256 | 0.167 | 196.6592 | 2949.888
257 | 0.167 | 197.4274 | 2961.411
258 | 0.167 | 198.1956 | 2972.934
259 | 0.167 | 198.9638 | 2984.457
260 | 0.167 | 199.732 | 2995.98
261 | 0.167 | 200.5002 | 3007.503
262 | 0.167 | 201.2684 | 3019.026
263 | 0.167 | 202.0366 | 3030.549
264 | 0.167 | 202.8048 | 3042.072
265 | 0.167 | 203.573 | 3053.595
266 | 0.167 | 204.3412 | 3065.118
267 | 0.167 | 205.1094 | 3076.641
268 | 0.167 | 205.8776 | 3088.164
269 | 0.167 | 206.6458 | 3099.687
270 | 0.166 | 206.172 | 3092.58
271 | 0.166 | 206.9356 | 3104.034
272 | 0.166 | 207.6992 | 3115.488
273 | 0.166 | 208.4628 | 3126.942
274 | 0.166 | 209.2264 | 3138.396
275 | 0.166 | 209.99 | 3149.85
276 | 0.166 | 210.7536 | 3161.304
277 | 0.166 | 211.5172 | 3172.758
278 | 0.166 | 212.2808 | 3184.212
279 | 0.166 | 213.0444 | 3195.666
280 | 0.166 | 213.808 | 3207.12
281 | 0.166 | 214.5716 | 3218.574
282 | 0.166 | 215.3352 | 3230.028
283 | 0.166 | 216.0988 | 3241.482
284 | 0.166 | 216.8624 | 3252.936
285 | 0.166 | 217.626 | 3264.39
286 | 0.166 | 218.3896 | 3275.844
287 | 0.166 | 219.1532 | 3287.298
288 | 0.166 | 219.9168 | 3298.752
289 | 0.166 | 220.6804 | 3310.206
290 | 0.165 | 220.11 | 3301.65
291 | 0.165 | 220.869 | 3313.035
292 | 0.165 | 221.628 | 3324.42
293 | 0.165 | 222.387 | 3335.805
294 | 0.165 | 223.146 | 3347.19
295 | 0.165 | 223.905 | 3358.575
296 | 0.165 | 224.664 | 3369.96
297 | 0.165 | 225.423 | 3381.345
298 | 0.165 | 226.182 | 3392.73
299 | 0.165 | 226.941 | 3404.115
300 | 0.165 | 227.7 | 3415.5
301 | 0.165 | 228.459 | 3426.885
302 | 0.165 | 229.218 | 3438.27
303 | 0.165 | 229.977 | 3449.655
304 | 0.165 | 230.736 | 3461.04
305 | 0.165 | 231.495 | 3472.425
306 | 0.165 | 232.254 | 3483.81
307 | 0.165 | 233.013 | 3495.195
308 | 0.165 | 233.772 | 3506.58
309 | 0.165 | 234.531 | 3517.965
310 | 0.164 | 233.864 | 3507.96
311 | 0.164 | 234.6184 | 3519.276
312 | 0.164 | 235.3728 | 3530.592
313 | 0.164 | 236.1272 | 3541.908
314 | 0.164 | 236.8816 | 3553.224
315 | 0.164 | 237.636 | 3564.54
316 | 0.164 | 238.3904 | 3575.856
317 | 0.164 | 239.1448 | 3587.172
318 | 0.164 | 239.8992 | 3598.488
319 | 0.164 | 240.6536 | 3609.804
320 | 0.164 | 241.408 | 3621.12
321 | 0.164 | 242.1624 | 3632.436
322 | 0.164 | 242.9168 | 3643.752
323 | 0.164 | 243.6712 | 3655.068
324 | 0.164 | 244.4256 | 3666.384
325 | 0.164 | 245.18 | 3677.7
326 | 0.164 | 245.9344 | 3689.016
327 | 0.164 | 246.6888 | 3700.332
328 | 0.164 | 247.4432 | 3711.648
329 | 0.164 | 248.1976 | 3722.964
330 | 0.164 | 248.952 | 3734.28
331 | 0.164 | 249.7064 | 3745.596
332 | 0.164 | 250.4608 | 3756.912
333 | 0.164 | 251.2152 | 3768.228
334 | 0.164 | 251.9696 | 3779.544
335 | 0.164 | 252.724 | 3790.86
336 | 0.164 | 253.4784 | 3802.176
337 | 0.164 | 254.2328 | 3813.492
338 | 0.164 | 254.9872 | 3824.808
339 | 0.164 | 255.7416 | 3836.124
340 | 0.164 | 256.496 | 3847.44
341 | 0.164 | 257.2504 | 3858.756
342 | 0.164 | 258.0048 | 3870.072
343 | 0.164 | 258.7592 | 3881.388
344 | 0.164 | 259.5136 | 3892.704
345 | 0.164 | 260.268 | 3904.02
346 | 0.164 | 261.0224 | 3915.336
347 | 0.164 | 261.7768 | 3926.652
348 | 0.164 | 262.5312 | 3937.968
349 | 0.164 | 263.2856 | 3949.284
350 | 0.163 | 262.43 | 3936.45
351 | 0.163 | 263.1798 | 3947.697
352 | 0.163 | 263.9296 | 3958.944
353 | 0.163 | 264.6794 | 3970.191
354 | 0.163 | 265.4292 | 3981.438
355 | 0.163 | 266.179 | 3992.685
356 | 0.163 | 266.9288 | 4003.932
357 | 0.163 | 267.6786 | 4015.179
358 | 0.163 | 268.4284 | 4026.426
359 | 0.163 | 269.1782 | 4037.673
360 | 0.163 | 269.928 | 4048.92