## Sheet1
Asset_name | Asset_code | network | network_element | voltage_highside | voltage_lowside | investment_description | reliability_criteria | latitude | longitude | latitude_end | longitude_end | res_cust_affected_no | res_cust_affected_percent | primary_driver | augmentation_invest | replacement_invest | connections_invest | other_invest | total_invest | cost_accuracy_plus | cost_accuracy_minus | annual_deferral | deferrable_invest | opex | project_timing | commitment_timing | summer_critical | winter_critical | spring_critical | autumn_critical | summer_nameplate_cap_mva | summer_secure_cap_mva | summer_acc_cap_yr_minus2_mva | summer_acc_cap_yr_minus1_mva | summer_acc_cap_yr0_mva | summer_acc_cap_yr1_mva | summer_acc_cap_yr2_mva | summer_acc_cap_yr3_mva | summer_acc_cap_yr4_mva | summer_acc_cap_yr5_mva | summer_acc_cap_yr6_mva | summer_acc_cap_yr7_mva | summer_acc_cap_yr8_mva | summer_acc_cap_yr9_mva | summer_acc_cap_yr10_mva | summer_load_yr1_poe50_mva | summer_load_yr2_poe50_mva | summer_load_yr3_poe50_mva | summer_load_yr4_poe50_mva | summer_load_yr5_poe50_mva | summer_load_yr6_poe50_mva | summer_load_yr7_poe50_mva | summer_load_yr8_poe50_mva | summer_load_yr9_poe50_mva | summer_load_yr10_poe50_mva | summer_load_yr1_poe10_mva | summer_load_yr2_poe10_mva | summer_load_yr3_poe10_mva | summer_load_yr4_poe10_mva | summer_load_yr5_poe10_mva | summer_load_yr6_poe10_mva | summer_load_yr7_poe10_mva | summer_load_yr8_poe10_mva | summer_load_yr9_poe10_mva | summer_load_yr10_poe10_mva | winter_nameplate_cap_mva | winter_secure_cap_mva | winter_acc_cap_yr_minus2_mva | winter_acc_cap_yr_minus1_mva | winter_acc_cap_yr0_mva | winter_acc_cap_yr1_mva | winter_acc_cap_yr2_mva | winter_acc_cap_yr3_mva | winter_acc_cap_yr4_mva | winter_acc_cap_yr5_mva | winter_acc_cap_yr6_mva | winter_acc_cap_yr7_mva | winter_acc_cap_yr8_mva | winter_acc_cap_yr9_mva | winter_acc_cap_yr10_mva | winter_load_yr1_poe50_mva | winter_load_yr2_poe50_mva | winter_load_yr3_poe50_mva | winter_load_yr4_poe50_mva | winter_load_yr5_poe50_mva | winter_load_yr6_poe50_mva | winter_load_yr7_poe50_mva | winter_load_yr8_poe50_mva | winter_load_yr9_poe50_mva | winter_load_yr10_poe50_mva | winter_load_yr1_poe10_mva | winter_load_yr2_poe10_mva | winter_load_yr3_poe10_mva | winter_load_yr4_poe10_mva | winter_load_yr5_poe10_mva | winter_load_yr6_poe10_mva | winter_load_yr7_poe10_mva | winter_load_yr8_poe10_mva | winter_load_yr9_poe10_mva | winter_load_yr10_poe10_mva | mapped_poe | load_at_risk_yr1_mw | load_at_risk_yr2_mw | load_at_risk_yr3_mw | load_at_risk_yr4_mw | load_at_risk_yr5_mw | EUSE_MWh_yr1 | EUSE_MWh_yr2 | EUSE_MWh_yr3 | EUSE_MWh_yr4 | EUSE_MWh_yr5 | EUSE_MWh_yr6 | EUSE_MWh_yr7 | EUSE_MWh_yr8 | EUSE_MWh_yr9 | EUSE_MWh_yr10 | hrs_exceedance_yr1 | hrs_exceedance_yr2 | hrs_exceedance_yr3 | hrs_exceedance_yr4 | hrs_exceedance_yr5 | hrs_exceedance_yr6 | hrs_exceedance_yr7 | hrs_exceedance_yr8 | hrs_exceedance_yr9 | hrs_exceedance_yr10 | EUSE_value_yr1 | EUSE_value_yr2 | EUSE_value_yr3 | EUSE_value_yr4 | EUSE_value_yr5 | EUSE_value_yr6 | EUSE_value_yr7 | EUSE_value_yr8 | EUSE_value_yr9 | EUSE_value_yr10 | summer_support_constraintyr_mw | summer_support_constraintyr_mva | summer_support_yr1_mva | summer_support_yr2_mva | summer_support_yr3_mva | summer_support_yr4_mva | summer_support_yr5_mva | summer_support_yr6_mva | summer_support_yr7_mva | summer_support_yr8_mva | summer_support_yr9_mva | summer_support_yr10_mva | winter_support_constraintyr_mw | winter_support_constraintyr_mva | winter_support_yr1_mva | winter_support_yr2_mva | winter_support_yr3_mva | winter_support_yr4_mva | winter_support_yr5_mva | winter_support_yr6_mva | winter_support_yr7_mva | winter_support_yr8_mva | winter_support_yr9_mva | winter_support_yr10_mva | power_factor | reactive_support_details | load_transfer_capability_mva | emergency_generation_mva | emergency_generation_mw | historic_emergency_generation_flag | connected_region1 | connected_region1_EF | connected_region2 | connected_region2_EF | connected_region3 | connected_region3_EF | connected_region4 | connected_region4_EF | connected_region5 | connected_region5_EF | connected_region6 | connected_region6_EF | connected_region7 | connected_region7_EF | connected_region8 | connected_region8_EF | connected_region9 | connected_region9_EF | connected_region10 | connected_region10_EF | connected_region11 | connected_region11_EF | connected_region12 | connected_region12_EF | connected_region13 | connected_region13_EF | connected_region14 | connected_region14_EF | connected_region15 | connected_region15_EF | connected_region16 | connected_region16_EF | connected_region17 | connected_region17_EF | connected_region18 | connected_region18_EF | connected_region19 | connected_region19_EF | connected_region20 | connected_region20_EF | connected_region21 | connected_region21_EF | connected_region22 | connected_region22_EF | connected_region23 | connected_region23_EF | connected_region24 | connected_region24_EF | connected_region25 | connected_region25_EF | connected_region26 | connected_region26_EF | connected_region27 | connected_region27_EF | connected_region28 | connected_region28_EF | connected_region29 | connected_region29_EF | connected_region30 | connected_region30_EF | template_version_v2.1
Airport West Zone Substation | AW | Jemena | ZS | 66 | 22 | No investment currently planned | economic/probabilistic | -37.7155 | 144.8858 | -37.7155 | 144.8858 | 20740 | 0.87811 | [13 empty] | TRUE | FALSE | FALSE | FALSE | 130 | 130 | 100.5 | 100.5 | 100.5 | 100.5 | 100.5 | 100.5 | 100.5 | 100.5 | 100.5 | 100.5 | 100.5 | 100.5 | 100.5 | 70.846 | 72.6829 | 74.7467 | 76.7723 | 77.2171 | 78.3208 | 79.6018 | 81.0607 | 81.8521 | 83.1056 | 75.0106 | 76.7808 | 78.9809 | 80.9275 | 80.9005 | 82.0787 | 83.4746 | 84.89 | 86.2529 | 87.3103 | 130 | 130 | 120.7 | 120.7 | 120.7 | 120.7 | 120.7 | 120.7 | 120.7 | 120.7 | 120.7 | 120.7 | 120.7 | 120.7 | 120.7 | 55.6329 | 58.7729 | 61.7663 | 64.1297 | 65.099 | 66.2265 | 67.3014 | 68.3802 | 69.4589 | 70.5392 | 58.2921 | 61.3894 | 64.506 | 66.9041 | 67.8726 | 69.0564 | 70.1655 | 71.2563 | 72.3564 | 73.4581 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.96757 |  | 19.929 | 0 | 0 | No
Broadmeadows Zone Substation | BD | Jemena | ZS | 66 | 22 | No investment currently planned | economic/probabilistic | -37.6654 | 144.943 | -37.6654 | 144.943 | 14617 | 0.85181 | [13 empty] | FALSE | TRUE | FALSE | FALSE | 123 | 123 | 123.7 | 123.7 | 123.7 | 123.7 | 123.7 | 123.7 | 123.7 | 123.7 | 123.7 | 123.7 | 123.7 | 123.7 | 123.7 | 71.7808 | 75.1083 | 77.9443 | 80.0467 | 80.5843 | 81.5683 | 82.7324 | 84.0761 | 85.2768 | 86.4267 | 75.4032 | 78.7292 | 81.7286 | 83.7367 | 84.3173 | 85.3908 | 86.6886 | 88.0007 | 89.2516 | 90.1771 | 123 | 123 | 125.1 | 125.1 | 125.1 | 125.1 | 125.1 | 125.1 | 125.1 | 125.1 | 125.1 | 125.1 | 125.1 | 125.1 | 125.1 | 74.8055 | 79.4407 | 83.3388 | 85.806 | 86.898 | 87.9154 | 88.9371 | 89.963 | 90.9933 | 92.0278 | 78.3879 | 83.1142 | 87.0781 | 89.5606 | 90.6427 | 91.7146 | 92.7645 | 93.7892 | 94.8314 | 95.878 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95774 |  | 34.2565 | 0 | 0 | No
Broadmeadows South Zone Substation | BMS | Jemena | ZS | 66 | 22 | No investment currently planned | economic/probabilistic | -37.6867 | 144.9416 | -37.6867 | 144.9416 | 4440 | 0.89516 | [13 empty] | TRUE | FALSE | FALSE | FALSE | 47.6 | 47.6 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 34.8794 | 35.0148 | 35.2153 | 35.5011 | 35.6468 | 36.0438 | 36.5189 | 37.0715 | 37.5601 | 38.0253 | 36.6407 | 36.6996 | 36.9188 | 37.1299 | 37.29 | 37.7241 | 38.2554 | 38.7917 | 39.2999 | 39.6647 | 47.6 | 47.6 | 39.6 | 39.6 | 39.6 | 39.6 | 39.6 | 39.6 | 39.6 | 39.6 | 39.6 | 39.6 | 39.6 | 39.6 | 39.6 | 33.6341 | 34.3748 | 35.0153 | 35.4055 | 35.7333 | 36.0794 | 36.426 | 36.7733 | 37.1213 | 37.4699 | 35.2306 | 35.9454 | 36.5646 | 36.9316 | 37.2496 | 37.614 | 37.9684 | 37.835 | 38.18 | 38.5258 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00056704 | 0.0035639 | 0.0089981 | 0.014351 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9 | 1.8 | 3 | 4.6 | 0 | 0 | 0 | 0 | 0 | 0 | 27.1643 | 170.7314 | 431.0569 | 687.5121 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.025284 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.97594 |  | 11.0505 | 0 | 0 | No
Braybrook Zone Substation | BY | Jemena | ZS | 66 | 22 | No investment currently planned | economic/probabilistic | -37.7824 | 144.8747 | -37.7824 | 144.8747 | 10583 | 0.92784 | [13 empty] | TRUE | FALSE | FALSE | FALSE | 45 | 45 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 32 | 45.3083 | 45.9879 | 46.9776 | 47.7919 | 48.4539 | 49.429 | 50.5245 | 51.7427 | 52.8892 | 54.0189 | 48.5801 | 49.1979 | 50.2685 | 51.0193 | 51.7363 | 52.8031 | 54.0206 | 55.2625 | 56.482 | 57.5132 | 45 | 45 | 39.6 | 39.6 | 39.6 | 39.6 | 39.6 | 39.6 | 39.6 | 39.6 | 39.6 | 39.6 | 39.6 | 39.6 | 39.6 | 32.8815 | 34.3619 | 35.9595 | 37.0246 | 38.0488 | 39.131 | 40.0453 | 40.9613 | 41.8664 | 42.7657 | 34.4423 | 35.9319 | 37.5505 | 38.6205 | 39.6632 | 40.7955 | 41.741 | 42.6748 | 43.6029 | 44.5245 | 10 | 12.1782 | 12.8001 | 13.7057 | 14.451 | 15.0567 | 7.5964 | 10.1923 | 16.3227 | 23.4097 | 31.6935 | 47.0956 | 68.4136 | 97.8648 | 135.4198 | 176.6243 | 182.9 | 202.8 | 238.8 | 262.6 | 291.1 | 330.9 | 388.7 | 454.4 | 523.2 | 609 | 363905.4496 | 488263.1771 | 781943.829 | 1121449.6983 | 1518287.2868 | 2256129.9659 | 3277375.3915 | 4688240.8441 | 6487323.2655 | 8461238.7715 | 12.1782 | 13.3083 | 13.3083 | 13.9879 | 14.9776 | 15.7919 | 16.4539 | 17.429 | 18.5245 | 19.7427 | 20.8892 | 22.0189 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.44533 | 1.3613 | 2.2664 | 0.91508 |  | 22.5963 | 0 | 0 | No
Coburg North Zone Substation | CN | Jemena | ZS | 66 | 22 | CN zone substation redevelopment | economic/probabilistic | -37.7209 | 144.9778 | -37.7209 | 144.9778 | 20803 | 0.90479 | Asset Condition |  | $50.2m |  |  | $50.2m | 0.3 | 0.3 | $2.8m | $50.2m |  | 47058 |  | TRUE | FALSE | FALSE | FALSE | 93 | 93 | 72.5 | 72.5 | 72.5 | 72.5 | 72.5 | 72.5 | 72.5 | 72.5 | 72.5 | 72.5 | 72.5 | 72.5 | 72.5 | 55.5778 | 58.6812 | 61.4048 | 63.1827 | 64.1336 | 64.8485 | 65.7041 | 66.6997 | 67.5799 | 68.4182 | 59.7007 | 62.9012 | 65.8434 | 67.5922 | 68.6252 | 69.4256 | 70.4055 | 71.2193 | 72.1434 | 72.807 | 93 | 93 | 83.6 | 83.6 | 83.6 | 83.6 | 83.6 | 83.6 | 83.6 | 83.6 | 83.6 | 83.6 | 83.6 | 83.6 | 83.6 | 50.539 | 54.9405 | 58.8168 | 61.1926 | 62.8798 | 63.8902 | 64.9032 | 65.9188 | 66.9369 | 67.7767 | 52.9461 | 57.4706 | 61.447 | 63.8619 | 65.5821 | 66.6438 | 67.5124 | 68.5224 | 69.5446 | 70.5696 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00059866 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28.6791 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.9695 |  | 23.6633 | 0 | 0 | No
Coolaroo Zone Substation | COO | Jemena | ZS | 66 | 22 | Establish new zone substation Craigieburn (CBN) | economic/probabilistic | -37.6421 | 144.934 | -37.7453 | 145.0329 | 13160 | 0.9746 | Capacity |  |  |  | $34.0m | $34.0m | 0.3 | 0.3 | $1.9m | $34.0m |  | 46692 |  | TRUE | FALSE | FALSE | FALSE | 60 | 60 | 42.2 | 42.2 | 42.2 | 42.2 | 42.2 | 42.2 | 42.2 | 42.2 | 42.2 | 42.2 | 42.2 | 42.2 | 42.2 | 47.3752 | 48.7089 | 50.0121 | 51.2795 | 51.876 | 52.7152 | 53.6757 | 54.7586 | 55.756 | 56.7272 | 51.3348 | 52.6612 | 54.0833 | 55.3225 | 55.9774 | 56.9109 | 57.999 | 59.1039 | 60.1754 | 61.0364 | 60 | 60 | 47.3 | 47.3 | 47.3 | 47.3 | 47.3 | 47.3 | 47.3 | 47.3 | 47.3 | 47.3 | 47.3 | 47.3 | 47.3 | 40.7184 | 43.2031 | 45.4873 | 47.2988 | 48.5468 | 49.7263 | 50.8362 | 51.9521 | 53.0686 | 54.1879 | 42.6511 | 45.177 | 47.4999 | 49.3376 | 50.6067 | 51.8414 | 52.9888 | 54.1254 | 55.2696 | 56.4165 | 10 | 5.1142 | 6.4323 | 7.7201 | 8.9725 | 9.5621 | 0.21298 | 0.322 | 0.45674 | 0.61604 | 0.71777 | 0.87701 | 1.0776 | 1.3357 | 1.6702 | 2.4672 | 18.1 | 23 | 29.2 | 38.1 | 44.2 | 48.7 | 56.9 | 68.9 | 78.2 | 86.7 | 10202.9737 | 15425.6297 | 21880.3316 | 29511.5723 | 34385.0435 | 42013.4481 | 51621.8211 | 63986.0224 | 80010.1458 | 118191.4782 | 5.1142 | 5.1752 | 5.1752 | 6.5089 | 7.8121 | 9.0795 | 9.676 | 10.5152 | 11.4757 | 12.5586 | 13.556 | 14.5272 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2468 | 2.4263 | 3.5362 | 4.6521 | 5.7686 | 0.98822 |  | 16.8806 | 0 | 0 | No
Coburg South Zone Substation | CS | Jemena | ZS | 66 | 22 | Replace CS 22kV switchgear (arc flash risk), 66kV isolators, 66kV CB, earth switch and transformer bushings | economic/probabilistic | -37.7425 | 144.9626 | -37.7425 | 144.9626 | 19994 | 0.92096 | Asset Condition |  | $19.6m |  |  | $19.6m | 0.3 | 0.3 | $1.1m | $19.6m |  | 47423 |  | TRUE | FALSE | FALSE | FALSE | 46.5 | 46.5 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 42.6229 | 44.0752 | 45.1811 | 46.071 | 46.6152 | 47.5712 | 48.646 | 49.8418 | 50.9678 | 52.078 | 46.7694 | 48.2541 | 49.4777 | 50.3317 | 50.9369 | 52.0079 | 53.2309 | 54.4789 | 55.705 | 56.7422 | 47.6 | 47.6 | 39.6 | 39.6 | 39.6 | 39.6 | 39.6 | 39.6 | 39.6 | 39.6 | 39.6 | 39.6 | 39.6 | 39.6 | 39.6 | 33.1319 | 35.4323 | 37.231 | 38.4088 | 39.3417 | 40.3832 | 41.3614 | 42.1566 | 43.1371 | 44.1252 | 34.7182 | 37.0658 | 38.8933 | 40.0795 | 41.0264 | 42.1167 | 42.9255 | 43.9217 | 44.9292 | 45.9442 | 10 | 4.4479 | 5.8453 | 6.9093 | 7.7655 | 8.2891 | 0.17059 | 0.74081 | 1.5234 | 2.0874 | 2.688 | 4.6616 | 7.549 | 11.9199 | 17.5189 | 24.4046 | 7.9 | 13.4 | 18.6 | 22.1 | 25.3 | 31.7 | 37.8 | 45.5 | 57.1 | 63.9 | 8172.0075 | 35488.7397 | 72980.7289 | 99995.4054 | 128770.0446 | 223315.4647 | 361637.9172 | 571027.4185 | 839247.5885 | 1169109.4476 | 4.4479 | 4.6229 | 4.6229 | 6.0752 | 7.1811 | 8.071 | 8.6152 | 9.5712 | 10.646 | 11.8418 | 12.9678 | 14.078 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.78315 | 1.7614 | 2.5566 | 3.5371 | 0.96215 |  | 12.2317 | 0 | 0 | No
East Preston Zone Substation Switch House B | EP B | Jemena | ZS | 66 | 6.6 | EP Stage 7: Conversion of EP Feeders tand distribution substations to 22kV. | economic/probabilistic | -37.7453 | 145.0329 | -37.7453 | 145.0328 | 3811 | 0.86811 | Asset Condition |  | $31.8m |  |  | $31.8m | 0.3 | 0.3 | $1.8m | $31.8m |  | 47058 |  | FALSE | TRUE | FALSE | FALSE | 27 | 27 | 28.5 | 28.5 | 28.5 | 28.5 | 28.5 | 28.5 | 28.5 | 28.5 | 28.5 | 28.5 | 28.5 | 28.5 | 28.5 | 16.8692 | 16.8461 | 16.8138 | 16.9539 | 17.0591 | 17.2503 | 17.4792 | 17.7456 | 17.9811 | 18.2055 | 17.4695 | 17.4056 | 17.3764 | 17.4794 | 17.5915 | 17.7977 | 18.0501 | 18.305 | 18.5466 | 18.7201 | 27 | 27 | 28.5 | 28.5 | 28.5 | 28.5 | 28.5 | 28.5 | 28.5 | 28.5 | 28.5 | 28.5 | 28.5 | 28.5 | 28.5 | 17.2084 | 17.5596 | 17.8204 | 18.0899 | 18.3623 | 18.6093 | 18.8569 | 19.1051 | 19.354 | 19.6034 | 18.0287 | 18.3661 | 18.6134 | 18.8747 | 19.1469 | 19.4068 | 19.6618 | 19.9111 | 20.1638 | 20.4172 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.95736 |  | 0 | 0 | 0 | No
East Preston Zone Substation | EPN | Jemena | ZS | 66 | 22 | No investment currently planned | economic/probabilistic | -37.7455 | 145.0327 | -37.7455 | 145.0327 | 6796 | 0.85657 | [13 empty] | TRUE | FALSE | FALSE | FALSE | 33 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27.3263 | 28.2531 | 28.9883 | 29.747 | 30.2401 | 30.5788 | 30.9844 | 31.4565 | 31.874 | 32.2717 | 29.3322 | 30.2624 | 31.0604 | 31.7999 | 32.3352 | 32.7147 | 33.1795 | 33.6488 | 34.0936 | 34.413 | 33 | 33 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25.0337 | 26.5808 | 27.8423 | 28.8846 | 29.7347 | 30.2719 | 30.7204 | 31.1639 | 31.5964 | 32.0204 | 26.2334 | 27.808 | 29.0876 | 30.1435 | 31.0107 | 31.5743 | 32.0363 | 32.4827 | 32.9221 | 33.3527 | 10 | 26.0154 | 26.8977 | 27.5976 | 28.32 | 28.7893 | 231.2372 | 241.8929 | 250.5516 | 258.2511 | 264.07 | 267.8987 | 271.6917 | 275.8746 | 279.9578 | 284.4061 | 8784 | 8784 | 8784 | 8784 | 8784 | 8784 | 8784 | 8784 | 8784 | 8784 | 11077486.8071 | 11587949.7262 | 12002744.5199 | 12371595.272 | 12650348.8175 | 12833764.7191 | 13015467.1191 | 13215851.5954 | 13411457.2288 | 13624556.5379 | 26.0154 | 27.3263 | 27.3263 | 28.2531 | 28.9883 | 29.747 | 30.2401 | 30.5788 | 30.9844 | 31.4565 | 31.874 | 32.2717 | 23.8327 | 25.0337 | 25.0337 | 25.0337 | 26.5808 | 27.8423 | 28.8846 | 29.7347 | 30.2719 | 30.7204 | 31.1639 | 31.5964 | 0.95203 |  | 11.2029 | 0 | 0 | No
Essendon Zone Substation | ES | Jemena | ZS | 66 | 11 | No investment currently planned | economic/probabilistic | -37.7541 | 144.8936 | -37.77 | 145.0204 | 15826 | 0.9316 | [13 empty] | TRUE | FALSE | FALSE | FALSE | 47.6 | 47.6 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 43.696 | 43.8873 | 44.327 | 45.043 | 45.49 | 46.3049 | 47.2303 | 48.2676 | 49.2317 | 50.1753 | 47.2943 | 47.3927 | 47.8791 | 48.5355 | 49.0271 | 49.9299 | 50.9729 | 52.034 | 53.0685 | 53.9181 | 47.6 | 47.6 | 39.6 | 39.6 | 39.6 | 39.6 | 39.6 | 39.6 | 39.6 | 39.6 | 39.6 | 39.6 | 39.6 | 39.6 | 39.6 | 34.3324 | 35.4881 | 36.6858 | 37.7336 | 38.6085 | 39.5248 | 40.4531 | 41.3935 | 42.3462 | 43.3113 | 35.9765 | 37.125 | 38.3254 | 39.3773 | 40.2645 | 41.2247 | 42.1855 | 43.1453 | 44.1233 | 45.114 | 10 | 5.5008 | 5.6855 | 6.1102 | 6.8016 | 7.2333 | 0.41739 | 0.43369 | 0.56756 | 1.0366 | 1.6562 | 3.5654 | 7.2857 | 12.5077 | 20.1217 | 30.0837 | 26.6 | 28.3 | 29 | 33.7 | 35.6 | 46.1 | 53.6 | 63.8 | 74 | 84.3 | 19995.0696 | 20776.1068 | 27189.2615 | 49660.4126 | 79340.4384 | 170801.0816 | 349025.3723 | 599183.7727 | 963937.6369 | 1441169.3492 | 5.5008 | 5.696 | 5.696 | 5.8873 | 6.327 | 7.043 | 7.49 | 8.3049 | 9.2303 | 10.2676 | 11.2317 | 12.1753 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.85307 | 1.7935 | 2.7462 | 0.96573 |  | 10.86 | 0 | 0 | No
Footscray East Zone Substation | FE | Jemena | ZS | 66 | 22 | No investment currently planned | economic/probabilistic | -37.8135 | 144.8961 | -37.8135 | 144.8961 | 12795 | 0.88534 | [13 empty] | TRUE | FALSE | FALSE | FALSE | 47.6 | 47.6 | 47.6 | 47.6 | 47.6 | 47.6 | 47.6 | 47.6 | 47.6 | 47.6 | 47.6 | 47.6 | 47.6 | 47.6 | 47.6 | 38.8491 | 39.0533 | 39.5444 | 40.5717 | 41.5309 | 42.7244 | 44.046 | 45.5014 | 46.9167 | 48.3406 | 40.8301 | 40.9525 | 41.4808 | 42.4625 | 43.4807 | 44.7586 | 46.1907 | 47.6692 | 49.1527 | 50.4899 | 47.6 | 47.6 | 47.6 | 47.6 | 47.6 | 47.6 | 47.6 | 47.6 | 47.6 | 47.6 | 47.6 | 47.6 | 47.6 | 47.6 | 47.6 | 38.287 | 39.3211 | 40.4715 | 41.8137 | 43.1911 | 44.589 | 45.9306 | 46.6198 | 47.958 | 49.3233 | 40.1549 | 41.1681 | 42.3127 | 43.6672 | 45.076 | 46.5397 | 47.2256 | 48.5772 | 49.96 | 51.3703 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.57469 | 4.3327 | 16.1511 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1.2 | 4.6 | 14.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27530.7567 | 207558.7218 | 773724.8549 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.74063 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.35797 | 0.92155 |  | 24.6921 | 0 | 0 | No
Fairfield Zone Substation | FF | Jemena | ZS | 22 | 6.6 | Replace FF No.3 transformer | economic/probabilistic | -37.77 | 145.0204 | -37.8152 | 144.8726 | 6337 | 0.92484 | Asset Condition |  | ($0 Committed Project) |  |  | ($0 Committed Project) | 0.3 | 0.3 | ($0 Committed Project) | ($0 Committed Project) |  | 46327 |  | TRUE | FALSE | FALSE | FALSE | 36 | 36 | 21.9 | 21.9 | 21.9 | 21.9 | 21.9 | 21.9 | 21.9 | 21.9 | 21.9 | 21.9 | 21.9 | 21.9 | 21.9 | 24.5107 | 25.2801 | 27.4508 | 29.6725 | 31.247 | 32.5067 | 33.361 | 34.3018 | 35.0672 | 35.8217 | 26.0897 | 26.8494 | 29.1651 | 31.4533 | 33.1303 | 34.4837 | 35.4216 | 36.3808 | 37.1898 | 37.8739 | 36 | 36 | 21.9 | 21.9 | 21.9 | 21.9 | 21.9 | 21.9 | 21.9 | 21.9 | 21.9 | 21.9 | 21.9 | 21.9 | 21.9 | 21.9245 | 23.3229 | 26.0878 | 28.7214 | 30.4699 | 32.0406 | 33.0275 | 34.0281 | 34.8946 | 35.7653 | 22.9652 | 24.3885 | 27.242 | 29.9594 | 31.7636 | 33.4056 | 34.4289 | 35.4551 | 36.3459 | 37.2408 | 10 | 2.5682 | 3.3251 | 5.4605 | 7.646 | 9.1949 | 0.33971 | 0.61132 | 2.0241 | 4.6866 | 7.4703 | 10.4805 | 12.7833 | 15.7178 | 19.6268 | 25.4277 | 35.4 | 56.5 | 129 | 241.4 | 328.6 | 418.8 | 480.7 | 549.8 | 627.8 | 736.4 | 16274.0411 | 29285.5618 | 96965.5351 | 224512.8919 | 357868.5551 | 502071.4755 | 612387.2617 | 752967.6828 | 940228.3613 | 1218120.899 | 2.5682 | 2.6107 | 2.6107 | 3.3801 | 5.5508 | 7.7725 | 9.347 | 10.6067 | 11.461 | 12.4018 | 13.1672 | 13.9217 | 0.024118 | 0.024517 | 0.024517 | 0.024517 | 1.4229 | 4.1878 | 6.8214 | 8.5699 | 10.1406 | 11.1275 | 12.1281 | 12.9946 | 0.98372 |  | 0 | 0 | 0 | No
Flemington Zone Substation | FT | Jemena | ZS | 66 | 11 | 3rd Transformer and 66kV Works at FT | economic/probabilistic | -37.7917 | 144.9319 | -37.7917 | 144.9319 | 13554 | 0.92614 | Capacity | $9.8m |  |  |  | $9.8m | 0.3 | 0.3 | $552k | $9.8m |  | 47423 |  | TRUE | FALSE | FALSE | FALSE | 45 | 45 | 34.8 | 34.8 | 34.8 | 34.8 | 34.8 | 34.8 | 34.8 | 34.8 | 34.8 | 34.8 | 34.8 | 34.8 | 34.8 | 39.5309 | 41.7028 | 44.3279 | 46.6696 | 48.4523 | 49.6931 | 51.0705 | 52.5893 | 54.049 | 55.5061 | 41.9843 | 44.1996 | 47.0021 | 49.3729 | 51.2732 | 52.6147 | 54.1238 | 55.6734 | 57.2156 | 58.5773 | 45 | 45 | 34.8 | 34.8 | 34.8 | 34.8 | 34.8 | 34.8 | 34.8 | 34.8 | 34.8 | 34.8 | 34.8 | 34.8 | 34.8 | 37.0047 | 40.2539 | 43.4399 | 46.313 | 48.9369 | 51.1411 | 52.8101 | 54.4791 | 56.107 | 57.7083 | 38.7946 | 41.7452 | 45.371 | 48.3261 | 51.0362 | 53.344 | 55.0771 | 56.7917 | 58.4701 | 60.12 | 10 | 4.5215 | 6.5973 | 9.1062 | 11.3443 | 13.0481 | 0.43569 | 1.2257 | 4.6595 | 24.0294 | 80.1271 | 164.6321 | 275.8827 | 434.8911 | 643.2897 | 909.9838 | 49.4 | 114.2 | 232.3 | 401.6 | 592.1 | 826.2 | 1115 | 1524.5 | 1992.2 | 2514.1 | 20871.6261 | 58717.6873 | 223216.0566 | 1151136.1211 | 3838511.1298 | 7886748.7934 | 13216241.3354 | 20833585.5136 | 30816977.7283 | 43593037.6476 | 4.5215 | 4.7309 | 4.7309 | 6.9028 | 9.5279 | 11.8696 | 13.6523 | 14.8931 | 16.2705 | 17.7893 | 19.249 | 20.7061 | 2.1071 | 2.2047 | 2.2047 | 2.2047 | 5.4539 | 8.6399 | 11.513 | 14.1369 | 16.3411 | 18.0101 | 19.6791 | 21.307 | 0.95574 |  | 4.7631 | 0 | 0 | No
Footscray West Zone Substation | FW | Jemena | ZS | 66 | 22 | Replace FW switchgear and relays | economic/probabilistic | -37.8152 | 144.8726 | -37.8152 | 144.8726 | 13511 | 0.94635 | Asset Condition |  | ($0 Committed Project) |  |  | ($0 Committed Project) | 0.3 | 0.3 | ($0 Committed Project) | ($0 Committed Project) |  | 46327 |  | TRUE | FALSE | FALSE | FALSE | 90 | 90 | 70.3 | 70.3 | 70.3 | 70.3 | 70.3 | 70.3 | 70.3 | 70.3 | 70.3 | 70.3 | 70.3 | 70.3 | 70.3 | 43.9763 | 51.2375 | 52.9048 | 54.1155 | 56.403 | 56.3986 | 56.5082 | 56.727 | 56.8368 | 56.9021 | 46.0772 | 53.5152 | 55.3107 | 56.4474 | 58.8549 | 58.8793 | 59.0464 | 59.21 | 59.3199 | 59.2051 | 90 | 90 | 77.2 | 77.2 | 77.2 | 77.2 | 77.2 | 77.2 | 77.2 | 77.2 | 77.2 | 77.2 | 77.2 | 77.2 | 77.2 | 41.1192 | 49.2176 | 51.9196 | 53.6928 | 56.6775 | 57.0547 | 57.2712 | 57.4679 | 57.6357 | 57.7796 | 43.1081 | 51.4752 | 54.2036 | 55.9828 | 59.0962 | 59.4967 | 59.7121 | 59.8882 | 60.0156 | 60.1445 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.94258 |  | 37.1525 | 0 | 0 | No
Heidelberg Zone Substation | HB | Jemena | ZS | 66 | 11 | No investment currently planned | economic/probabilistic | -37.7591 | 145.0706 | -37.7591 | 145.0706 | 8717 | 0.90266 | [13 empty] | TRUE | FALSE | FALSE | FALSE | 45 | 45 | 29.2 | 29.2 | 29.2 | 29.2 | 29.2 | 29.2 | 29.2 | 29.2 | 29.2 | 29.2 | 29.2 | 29.2 | 29.2 | 27.1349 | 27.2771 | 27.4733 | 27.8344 | 28.0969 | 28.4352 | 28.8352 | 29.2966 | 29.7085 | 30.1028 | 29.0509 | 29.1376 | 29.3541 | 29.6697 | 29.9555 | 30.331 | 30.7845 | 31.2428 | 31.6794 | 32.0022 | 45 | 45 | 35.6 | 35.6 | 35.6 | 35.6 | 35.6 | 35.6 | 35.6 | 35.6 | 35.6 | 35.6 | 35.6 | 35.6 | 35.6 | 19.9884 | 20.7525 | 21.4601 | 22.1169 | 22.7435 | 23.3437 | 23.7798 | 24.2063 | 24.6123 | 25.0025 | 20.9372 | 21.7007 | 22.4097 | 23.0702 | 23.7085 | 24.3366 | 24.7867 | 25.219 | 25.6332 | 26.0307 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00033232 | 0.0016355 | 0.0041503 | 0.0095814 | 0.017469 | 0.026977 | 0.039886 | 0.056576 | 0 | 0 | 0.6 | 1.2 | 2.4 | 3.9 | 4.5 | 6.2 | 8.6 | 13.8 | 0 | 0 | 15.9201 | 78.3476 | 198.8219 | 458.9985 | 836.8662 | 1292.3303 | 1910.728 | 2710.2893 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.096611 | 0.50852 | 0.90276 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.97914 |  | 0 | 0 | 0 | No
North Heidelberg Zone Substation | NH | Jemena | ZS | 66 | 22 | No investment currently planned | economic/probabilistic | -37.7295 | 145.068 | -37.7295 | 145.068 | 15340 | 0.95791 | [13 empty] | TRUE | FALSE | FALSE | FALSE | 93 | 93 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 75.2 | 51.0817 | 47.4177 | 48.2122 | 49.0248 | 49.3669 | 50.1133 | 50.9738 | 51.9494 | 52.8429 | 53.7105 | 54.8148 | 50.4837 | 51.6187 | 52.3678 | 52.7453 | 53.5721 | 54.5435 | 55.5296 | 56.483 | 57.237 | 93 | 93 | 76 | 76 | 76 | 76 | 76 | 76 | 76 | 76 | 76 | 76 | 76 | 76 | 76 | 42.7237 | 39.9126 | 41.7786 | 42.9676 | 43.7834 | 44.5879 | 45.4491 | 46.3147 | 47.1813 | 48.0503 | 44.6574 | 41.7498 | 43.6415 | 44.7235 | 45.5375 | 46.4867 | 47.3769 | 48.2565 | 49.1435 | 50.0327 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.96477 |  | 0.57158 | 0 | 0 | No
North Essendon Zone Substation | NS | Jemena | ZS | 22 | 11 | No investment currently planned | economic/probabilistic | -37.7511 | 144.9289 | -37.7511 | 144.9289 | 10471 | 0.89236 | [13 empty] | TRUE | FALSE | FALSE | FALSE | 54 | 54 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36.1743 | 36.5681 | 37.8102 | 39.5068 | 40.8463 | 42.0801 | 43.4126 | 44.6795 | 45.8955 | 47.1079 | 40.8782 | 41.2304 | 42.6409 | 44.4492 | 45.9653 | 47.3768 | 48.9198 | 50.2922 | 51.6565 | 52.86 | 54 | 54 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 36 | 29.0398 | 30.1601 | 31.967 | 33.9134 | 35.6054 | 36.9357 | 38.1914 | 39.278 | 40.3766 | 41.4896 | 30.4182 | 31.5381 | 33.3814 | 35.3752 | 37.1162 | 38.5068 | 39.8086 | 40.9212 | 42.0512 | 43.1959 | 10 | 0.17175 | 0.55978 | 1.7835 | 3.4552 | 4.7749 | 0.1182 | 0.1412 | 0.26278 | 0.50527 | 0.79036 | 1.1654 | 1.6886 | 2.276 | 2.9645 | 3.7561 | 7.9 | 10.6 | 16.6 | 23.9 | 36.5 | 49.6 | 65.2 | 79.2 | 98.9 | 117.8 | 5662.3121 | 6764.4334 | 12588.6649 | 24205.3376 | 37862.6164 | 55829.007 | 80890.825 | 109031.7598 | 142013.7951 | 179936.487 | 0.17175 | 0.17432 | 0.17432 | 0.56815 | 1.8102 | 3.5068 | 4.8463 | 6.0801 | 7.4126 | 8.6795 | 9.8955 | 11.1079 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.93574 | 2.1914 | 3.278 | 4.3766 | 0.98528 |  | 10.2503 | 0 | 0 | No
Newport Zone Substation | NT | Jemena | ZS | 66 | 22 | No investment currently planned | economic/probabilistic | -37.8399 | 144.8938 | -37.8399 | 144.8938 | 12394 | 0.92846 | [13 empty] | TRUE | FALSE | FALSE | FALSE | 57 | 57 | 41.5 | 41.5 | 41.5 | 41.5 | 41.5 | 41.5 | 41.5 | 41.5 | 41.5 | 41.5 | 41.5 | 41.5 | 41.5 | 37.004 | 37.4712 | 38.3159 | 39.284 | 39.6325 | 40.2299 | 40.9179 | 41.6971 | 42.4099 | 43.1014 | 39.6527 | 40.0631 | 40.9759 | 41.9121 | 42.2923 | 42.9506 | 43.7235 | 44.0904 | 44.8406 | 45.4335 | 57 | 57 | 41.5 | 41.5 | 41.5 | 41.5 | 41.5 | 41.5 | 41.5 | 41.5 | 41.5 | 41.5 | 41.5 | 41.5 | 41.5 | 31.5626 | 32.8161 | 34.2887 | 35.535 | 36.2423 | 36.933 | 37.6296 | 38.3322 | 39.041 | 39.7558 | 33.0607 | 34.3154 | 35.8059 | 37.0667 | 37.7802 | 38.5039 | 39.2229 | 39.9358 | 40.6602 | 41.3908 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00053068 | 0.0010886 | 0.0027694 | 0.0063489 | 0.0093185 | 0.018517 | 0.031217 | 0 | 0 | 0 | 0.3 | 0.6 | 0.6 | 1.5 | 2.2 | 4.1 | 6.6 | 0 | 0 | 0 | 25.4223 | 52.148 | 132.6686 | 304.1471 | 446.4066 | 887.0424 | 1495.4547 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.19708 | 0.90994 | 1.6014 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.99063 |  | 5.7158 | 0 | 0 | No
Preston Zone Substation | PTN | Jemena | ZS | 66 | 22 | No investment currently planned | economic/probabilistic | -37.737 | 145.0006 | -37.737 | 145.0006 | 10369 | 0.88677 | [13 empty] | TRUE | FALSE | FALSE | FALSE | 47.6 | 47.6 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 28.2194 | 33.8376 | 33.9621 | 34.394 | 34.7249 | 35.2521 | 35.8595 | 36.5475 | 37.177 | 37.7878 | 30.184 | 36.1154 | 36.2569 | 36.6309 | 36.9909 | 37.5711 | 38.2523 | 38.9433 | 39.6108 | 40.1383 | 47.6 | 47.6 | 39.6 | 39.6 | 39.6 | 39.6 | 39.6 | 39.6 | 39.6 | 39.6 | 39.6 | 39.6 | 39.6 | 39.6 | 39.6 | 24.5201 | 30.6638 | 31.369 | 32.0761 | 32.7614 | 33.4525 | 34.0706 | 34.6887 | 35.3015 | 35.9112 | 24.8849 | 31.0502 | 31.7716 | 32.4113 | 33.1103 | 33.8252 | 34.4803 | 35.0673 | 35.6837 | 36.1897 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00032711 | 0.0012228 | 0.0021857 | 0.0048184 | 0 | 0 | 0 | 0 | 0 | 0 | 0.3 | 0.3 | 0.6 | 1.8 | 0 | 0 | 0 | 0 | 0 | 0 | 15.6705 | 58.578 | 104.7077 | 230.8265 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.98449 |  | 13.4511 | 0 | 0 | No
Pascoe Vale Zone Substation | PV | Jemena | ZS | 66 | 22 | No investment currently planned | economic/probabilistic | -37.7224 | 144.933 | -37.7224 | 144.933 | 21188 | 0.96265 | [13 empty] | TRUE | FALSE | FALSE | FALSE | 64 | 64 | 45.6 | 45.6 | 45.6 | 45.6 | 45.6 | 45.6 | 45.6 | 45.6 | 45.6 | 45.6 | 45.6 | 45.6 | 45.6 | 37.4129 | 37.4833 | 37.7764 | 38.3394 | 38.7167 | 39.1516 | 39.672 | 40.2773 | 40.8125 | 41.322 | 41.9812 | 41.964 | 42.3024 | 42.83 | 43.2603 | 43.768 | 44.3895 | 44.5929 | 45.1717 | 45.5874 | 64 | 64 | 45.6 | 45.6 | 45.6 | 45.6 | 45.6 | 45.6 | 45.6 | 45.6 | 45.6 | 45.6 | 45.6 | 45.6 | 45.6 | 32.3776 | 33.3806 | 34.4408 | 35.4481 | 36.3634 | 37.1504 | 37.7971 | 38.4356 | 39.0564 | 39.6637 | 33.9144 | 34.9058 | 35.9646 | 36.9761 | 37.9064 | 38.7306 | 39.3976 | 40.0435 | 40.6763 | 41.2949 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.96475 |  | 0.95263 | 0 | 0 | No
Sunbury Zone Substation | SBY | Jemena | ZS | 66 | 22 | Upgrade SBY No.1 and No.3 transformers to 20/33MVA | economic/probabilistic | -37.5856 | 144.7222 | -37.8083 | 144.8485 | 17521 | 0.94189 | Capacity | $12.3m |  |  |  | $12.3m | 0.3 | 0.3 | $693k | $12.3m |  | 46692 |  | TRUE | FALSE | FALSE | FALSE | 65 | 65 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 48.1166 | 51.1705 | 53.4068 | 55.3727 | 56.4235 | 57.6791 | 59.0812 | 60.6336 | 62.1076 | 63.5676 | 51.5302 | 54.6793 | 57.0837 | 59.0455 | 60.1785 | 61.5481 | 63.1003 | 64.6873 | 66.2544 | 67.6051 | 65 | 65 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 42.3953 | 46.5569 | 49.8048 | 52.3151 | 54.1367 | 55.9759 | 57.4761 | 58.979 | 60.4589 | 61.9257 | 44.4145 | 48.6916 | 51.9225 | 54.5715 | 56.4362 | 58.3602 | 59.9139 | 61.4508 | 62.9716 | 64.4781 | 10 | 10.0023 | 13.0216 | 15.2326 | 17.1763 | 18.2152 | 1.3428 | 2.8896 | 4.724 | 6.6974 | 8.1651 | 9.9707 | 11.9386 | 14.2261 | 17.0525 | 20.2377 | 63.4 | 105.4 | 152.8 | 192.9 | 217.6 | 251.6 | 288.9 | 331.7 | 370.1 | 420.2 | 64328.6401 | 138427.8663 | 226306.4706 | 320842.998 | 391149.8649 | 477648.2984 | 571920.704 | 681503.4793 | 816902.6403 | 969492.5081 | 10.0023 | 10.1166 | 10.1166 | 13.1705 | 15.4068 | 17.3727 | 18.4235 | 19.6791 | 21.0812 | 22.6336 | 24.1076 | 25.5676 | 4.3456 | 4.3953 | 4.3953 | 4.3953 | 8.5569 | 11.8048 | 14.3151 | 16.1367 | 17.9759 | 19.4761 | 20.979 | 22.4589 | 0.9887 |  | 5.7158 | 0 | 0 | No
Sydenham Zone Substation | SHM | Jemena | ZS | 66 | 22 | Replace REFCL at SHM | economic/probabilistic | -37.6761 | 144.7535 | -37.6761 | 144.7535 | 18619 | 0.97523 | Asset Condition |  |  |  | ($0 Committed Project) | ($0 Committed Project) | 0.3 | 0.3 | ($0 Committed Project) | ($0 Committed Project) |  | 45962 |  | TRUE | FALSE | FALSE | FALSE | 47.6 | 47.6 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 44.0105 | 46.5829 | 48.919 | 50.9067 | 52.1201 | 53.5959 | 55.225 | 57.0135 | 58.7477 | 60.4879 | 46.5908 | 49.3891 | 51.8818 | 53.8646 | 55.1609 | 56.7521 | 58.5301 | 60.3604 | 62.1924 | 63.8399 | 47.6 | 47.6 | 39.6 | 39.6 | 39.6 | 39.6 | 39.6 | 39.6 | 39.6 | 39.6 | 39.6 | 39.6 | 39.6 | 39.6 | 39.6 | 34.0975 | 37.895 | 40.9987 | 43.6744 | 45.7094 | 47.8905 | 49.5835 | 51.2843 | 52.9545 | 54.608 | 35.7159 | 39.4103 | 42.8144 | 45.5596 | 47.6522 | 49.9315 | 51.6875 | 53.4344 | 55.156 | 56.8592 | 10 | 5.9183 | 8.4512 | 10.7515 | 12.7087 | 13.9034 | 0.16854 | 1.7581 | 7.6077 | 17.6057 | 25.1926 | 38.5824 | 60.3435 | 89.5877 | 124.4598 | 168.6204 | 10.9 | 16.9 | 33.1 | 47 | 56.2 | 66.4 | 78.8 | 97.6 | 118.1 | 137.5 | 8073.8061 | 84220.4227 | 364449.3728 | 843405.5466 | 1206859.4344 | 1848298.8391 | 2890772.1618 | 4291722.6497 | 5962281.1774 | 8077809.1919 | 5.9183 | 6.0105 | 6.0105 | 8.5829 | 10.919 | 12.9067 | 14.1201 | 15.5959 | 17.225 | 19.0135 | 20.7477 | 22.4879 | 0 | 0 | 0 | 0 | 0 | 1.3987 | 4.0744 | 6.1094 | 8.2905 | 9.9835 | 11.6843 | 13.3545 | 0.98465 |  | 2.6674 | 0 | 0 | No
Somerton Zone Substation | ST | Jemena | ZS | 66 | 22 | Establish a new zone substation at Craigieburn (CBN) | economic/probabilistic | -37.6225 | 144.9486 | -37.6502 | 144.9367 | 18355 | 0.8753 | Capacity |  |  |  | $34.0m | $34.0m | 0.3 | 0.3 | $1.9m | $34.0m |  | 46692 |  | FALSE | TRUE | FALSE | FALSE | 95.2 | 95.2 | 79.7 | 79.7 | 79.7 | 79.7 | 79.7 | 79.7 | 79.7 | 79.7 | 79.7 | 79.7 | 79.7 | 79.7 | 79.7 | 77.495 | 82.1532 | 87.1991 | 91.6347 | 94.7408 | 96.9857 | 99.4867 | 102.2509 | 104.8863 | 107.5035 | 80.658 | 85.3108 | 90.573 | 94.9504 | 98.1886 | 100.5649 | 103.2501 | 105.9993 | 108.7212 | 111.0872 | 95.2 | 95.2 | 89.3 | 89.3 | 89.3 | 89.3 | 89.3 | 89.3 | 89.3 | 89.3 | 89.3 | 89.3 | 89.3 | 89.3 | 89.3 | 78.4801 | 84.0416 | 89.936 | 94.5664 | 98.1622 | 100.4868 | 102.6465 | 104.8319 | 107.0288 | 109.2432 | 82.0015 | 87.8877 | 93.9279 | 98.6593 | 102.3469 | 104.7825 | 107.0161 | 109.2417 | 111.4937 | 113.763 | 10 | 0 | 2.3444 | 7.1665 | 11.4054 | 14.3737 | 0.0037044 | 0.10216 | 0.72811 | 5.7471 | 28.0341 | 65.4385 | 128.8117 | 240.7572 | 410.8634 | 647.5796 | 0.9 | 7 | 36.6 | 88.1 | 149.2 | 198 | 269.9 | 380.7 | 524 | 706.4 | 177.4618 | 4893.8755 | 34880.1098 | 275318.2947 | 1342980.4186 | 3134849.8894 | 6170761.4996 | 11533543.3826 | 19682527.82 | 31022486.8997 | 0 | 0 | 0 | 2.4532 | 7.4991 | 11.9347 | 15.0408 | 17.2857 | 19.7867 | 22.5509 | 25.1863 | 27.8035 | 0 | 0 | 0 | 0 | 0 | 0.63603 | 5.2664 | 8.8622 | 11.1868 | 13.3465 | 15.5319 | 17.7288 | 0.95565 |  | 15.242 | 0 | 0 | No
Tottenham Zone Substation | TH | Jemena | ZS | 66 | 22 | No investment currently planned | economic/probabilistic | -37.8084 | 144.8486 | -37.8084 | 144.8486 | 2398 | 0.73199 | [13 empty] | FALSE | TRUE | FALSE | FALSE | 47.6 | 47.6 | 47.6 | 47.6 | 47.6 | 47.6 | 47.6 | 47.6 | 47.6 | 47.6 | 47.6 | 47.6 | 47.6 | 47.6 | 47.6 | 21.4936 | 19.1517 | 21.1975 | 22.874 | 22.765 | 22.8122 | 22.9083 | 23.0517 | 22.3475 | 22.4182 | 21.8353 | 19.4092 | 21.4883 | 22.3299 | 23.0239 | 22.2887 | 22.3963 | 22.5031 | 22.5901 | 22.5925 | 47.6 | 47.6 | 47.6 | 47.6 | 47.6 | 47.6 | 47.6 | 47.6 | 47.6 | 47.6 | 47.6 | 47.6 | 47.6 | 47.6 | 47.6 | 29.8576 | 28.1665 | 30.3255 | 31.987 | 32.0538 | 32.1173 | 32.1777 | 32.2351 | 32.2894 | 32.3408 | 31.2981 | 29.4629 | 31.6919 | 33.3998 | 33.4477 | 33.5177 | 33.5747 | 33.6179 | 33.6629 | 33.7051 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.8804 |  | 22.2915 | 0 | 0 | No
Tullamarine Zone Substation | TMA | Jemena | ZS | 66 | 22 | No investment currently planned | economic/probabilistic | -37.7116 | 144.859 | -37.7116 | 144.859 | 1321 | 0.48371 | [13 empty] | FALSE | TRUE | FALSE | FALSE | 49.5 | 49.5 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 21.2578 | 21.4464 | 21.5627 | 21.9532 | 22.2582 | 22.6161 | 23.0258 | 22.6778 | 23.0893 | 23.4903 | 22.4876 | 22.6361 | 22.7642 | 22.3243 | 22.6392 | 23.0151 | 23.4539 | 23.8999 | 24.3328 | 24.681 | 49.5 | 49.5 | 39.6 | 39.6 | 39.6 | 39.6 | 39.6 | 39.6 | 39.6 | 39.6 | 39.6 | 39.6 | 39.6 | 39.6 | 39.6 | 21.4864 | 22.0397 | 22.4309 | 22.8898 | 23.3147 | 23.658 | 24.0047 | 24.3547 | 24.708 | 25.0646 | 22.5063 | 23.0467 | 23.4233 | 23.8764 | 24.3039 | 24.6643 | 25.0212 | 25.3735 | 25.7328 | 26.0955 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.96551 |  | 9.069 | 0 | 0 | No
Yarraville Zone Substation | YVE | Jemena | ZS | 66 | 22 | No investment currently planned | economic/probabilistic | -37.8225 | 144.8938 | -37.8225 | 144.8938 | 5564 | 0.88458 | [13 empty] | FALSE | TRUE | FALSE | FALSE | 49.5 | 49.5 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 38 | 31.2968 | 31.9619 | 32.6192 | 33.5196 | 34.2133 | 34.9018 | 35.6754 | 36.5356 | 37.3451 | 38.1428 | 33.1361 | 33.7642 | 34.4667 | 35.3345 | 36.0731 | 36.8169 | 37.6658 | 38.5317 | 39.382 | 40.101 | 49.5 | 49.5 | 39.6 | 39.6 | 39.6 | 39.6 | 39.6 | 39.6 | 39.6 | 39.6 | 39.6 | 39.6 | 39.6 | 39.6 | 39.6 | 32.6687 | 33.9554 | 35.1071 | 36.2049 | 37.1786 | 37.9422 | 38.7173 | 39.5041 | 40.3029 | 41.1136 | 34.2193 | 35.5069 | 36.6604 | 37.7655 | 38.7561 | 39.556 | 40.3567 | 41.1567 | 41.9744 | 42.8045 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.0011777 | 0.0049364 | 0.014391 | 0.03015 | 0 | 0 | 0 | 0 | 0 | 0 | 0.6 | 1.5 | 3.5 | 6.2 | 0 | 0 | 0 | 0 | 0 | 0 | 56.4178 | 236.4785 | 689.3913 | 1444.3349 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.14276 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.70285 | 0.99296 |  | 26.102 | 0 | 0 | No
BD008 Feeder | BD0-008 | Jemena | DF | 22 | 22 | Augment feeder BD0-008 | economic/probabilistic | -37.6654 | 144.943 | -37.657 | 144.9695 | 213 | 0.24912 | Capacity | $1.8m |  |  |  | $1.8m | 0.3 | 0.3 | $104k | $1.8m |  | 46327 |  | FALSE | TRUE | FALSE | FALSE | 11.6221 | 11.6221 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.9123 | 9.3571 | 9.7377 | 9.9173 | 9.9626 | 10.0826 | 10.2244 | 10.388 | 10.534 | 10.6738 | 9.0449 | 9.475 | 9.8627 | 10.0209 | 10.0687 | 10.1949 | 10.3474 | 10.5014 | 10.6481 | 10.7566 | 11.6221 | 11.6221 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.7292 | 10.2493 | 10.665 | 10.7882 | 10.799 | 10.8207 | 10.8424 | 10.8641 | 10.8858 | 10.9077 | 10.191 | 10.7176 | 11.1369 | 11.2532 | 11.2573 | 11.2809 | 11.3015 | 11.3186 | 11.3373 | 11.3562 | 10 | 0 | 0 | 0.32268 | 1.3255 | 1.8192 | 0.0011979 | 0.042313 | 0.63551 | 1.9596 | 2.7836 | 3.0707 | 3.6067 | 4.3241 | 5.18 | 6.0853 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 57.3855 | 2027.0029 | 30444.3617 | 93876.2454 | 133346.7874 | 147104.1895 | 172781.9266 | 207146.683 | 248148.8484 | 291519.2458 | 0 | 0 | 8.9123 | 9.3571 | 9.7377 | 9.9173 | 9.9626 | 10.0826 | 10.2244 | 10.388 | 10.534 | 10.6738 | 0 | 0 | 9.7292 | 10.2493 | 10.665 | 10.7882 | 10.799 | 10.8207 | 10.8424 | 10.8641 | 10.8858 | 10.9077 | 0.94755 | 0 | 10.876 | 0 | 0 | No
ES011 Feeder | ES0-011 | Jemena | DF | 11 | 11 | Establish new feeder ES0-031 | economic/probabilistic | -37.7541 | 144.8936 | -37.733679 | 144.8898 | 1064 | 0.81036 | Capacity |  |  |  | $3.9m | $3.9m | 0.3 | 0.3 | $220k | $3.9m |  | 46692 |  | TRUE | FALSE | FALSE | FALSE | 5.811 | 5.811 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.2264 | 5.5861 | 5.8387 | 6.0728 | 6.144 | 6.2683 | 6.3914 | 6.5293 | 6.6575 | 6.7828 | 5.6594 | 6.0353 | 6.3097 | 6.5472 | 6.6253 | 6.7626 | 6.9014 | 7.0426 | 7.1802 | 7.2932 | 5.811 | 5.811 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.4455 | 4.8779 | 5.2063 | 5.4751 | 5.6115 | 5.7609 | 5.8976 | 6.0359 | 6.176 | 6.3179 | 4.6565 | 5.1008 | 5.4367 | 5.7111 | 5.8496 | 6.006 | 6.1473 | 6.2884 | 6.4322 | 6.5777 | 10 | 4.1957 | 4.833 | 5.0469 | 5.2864 | 5.4206 | 1.4385 | 2.107 | 3.4259 | 5.7343 | 7.074 | 9.4736 | 12.551 | 16.7603 | 22.0042 | 28.6975 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 68914.0409 | 100936.9904 | 164117.6652 | 274702.0004 | 338883.3589 | 453835.8959 | 601259.4447 | 802907.1761 | 1054116.1512 | 1374764.0687 | 0 | 0 | 5.2264 | 5.5861 | 5.8387 | 6.0728 | 6.144 | 6.2683 | 6.3914 | 6.5293 | 6.6575 | 6.7828 | 0 | 0 | 4.4455 | 4.8779 | 5.2063 | 5.4751 | 5.6115 | 5.7609 | 5.8976 | 6.0359 | 6.176 | 6.3179 | 0.94457 | 0 | 1.2175 | 0 | 0 | No
FF096 Feeder | FF0-096 | Jemena | DF | 6.6 | 6.6 | Augment feeder FF0-096 | economic/probabilistic | -37.77 | 145.0204 | -37.77 | 145.0199 | 0 |  | Capacity | $100k |  |  |  | $100k | 0.3 | 0.3 | $5.6k | $100k |  | 46327 |  | TRUE | FALSE | FALSE | FALSE | 6.7446 | 6.7446 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.533 | 1.2024 | 2.3955 | 3.719 | 4.7486 | 5.3269 | 5.6197 | 5.7267 | 5.8246 | 5.9195 | 0.57573 | 1.2959 | 2.5824 | 3.9997 | 5.1079 | 5.7328 | 6.0532 | 6.1617 | 6.2665 | 6.3493 | 6.7446 | 6.7446 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.49664 | 1.1471 | 2.3311 | 3.6578 | 4.7305 | 5.3396 | 5.6555 | 5.7738 | 5.8932 | 6.0136 | 0.52022 | 1.1995 | 2.4342 | 3.8154 | 4.9312 | 5.5667 | 5.895 | 6.0154 | 6.1376 | 6.2609 | 10 | 0.56427 | 1.2701 | 2.531 | 3.9201 | 5.0063 | 0.015517 | 0.035452 | 0.071418 | 0.1115 | 0.14341 | 0.16146 | 0.17075 | 0.17414 | 0.17747 | 0.18071 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 743.3286 | 1698.3354 | 3421.2902 | 5341.3696 | 6869.9323 | 7734.9396 | 8179.633 | 8342.3673 | 8501.7075 | 8656.7591 | 0 | 0 | 0.533 | 1.2024 | 2.3955 | 3.719 | 4.7486 | 5.3269 | 5.6197 | 5.7267 | 5.8246 | 5.9195 | 0 | 0 | 0.49664 | 1.1471 | 2.3311 | 3.6578 | 4.7305 | 5.3396 | 5.6555 | 5.7738 | 5.8932 | 6.0136 | 0.9801 | 0 | 0 | 0 | 0 | No
FF93 Feeder | FF0-093 | Jemena | DF | 6.6 | 6.6 | Augment feeder FF0-093 | economic/probabilistic | -37.77 | 145.0204 | -37.784475 | 145.0336 | 1267 | 0.97088 | Capacity | $1.1m |  |  |  | $1.1m | 0.3 | 0.3 | $62k | $1.1m |  | 46692 |  | TRUE | FALSE | FALSE | FALSE | 3.258 | 3.258 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.9399 | 2.9483 | 2.9628 | 2.9918 | 3.0174 | 3.0782 | 3.1464 | 3.2222 | 3.2936 | 3.364 | 3.1756 | 3.1775 | 3.1939 | 3.2175 | 3.2458 | 3.3127 | 3.3891 | 3.467 | 3.5435 | 3.6082 | 3.258 | 3.258 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.5365 | 2.6135 | 2.6831 | 2.7395 | 2.799 | 2.8732 | 2.9486 | 3.0253 | 3.1032 | 3.1824 | 2.6569 | 2.7329 | 2.8019 | 2.8575 | 2.9177 | 2.9954 | 3.0735 | 3.1519 | 3.2319 | 3.3132 | 10 | 0 | 0 | 0 | 1.7941 | 2.4626 | 0 | 0 | 0 | 0.22678 | 2.3769 | 3.3151 | 3.9634 | 4.5998 | 5.4001 | 6.4098 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 0 | 0 | 0 | 10864.1318 | 113867.8047 | 158810.2382 | 189870.0722 | 220353.8362 | 258694.2975 | 307061.7035 | 0 | 0 | 2.9399 | 2.9483 | 2.9628 | 2.9918 | 3.0174 | 3.0782 | 3.1464 | 3.2222 | 3.2936 | 3.364 | 0 | 0 | 2.5365 | 2.6135 | 2.6831 | 2.7395 | 2.799 | 2.8732 | 2.9486 | 3.0253 | 3.1032 | 3.1824 | 0.9801 | 0 | 5.1604 | 0 | 0 | No
FT011 Feeder | FT0-011 | Jemena | DF | 11 | 11 | Augment feeder FT0-011 | economic/probabilistic | -37.7917 | 144.9319 | -37.7916 | 144.932 | 989 | 0.95371 | Capacity | $134k |  |  |  | $134k | 0.3 | 0.3 | $7.5k | $134k |  | 47423 |  | FALSE | TRUE | FALSE | FALSE | 5.811 | 5.811 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.8135 | 4.785 | 4.7879 | 4.8443 | 4.898 | 4.9719 | 5.0569 | 5.1532 | 5.2413 | 5.3268 | 4.8852 | 4.8453 | 4.8494 | 4.8949 | 4.9502 | 5.0273 | 5.1177 | 5.2095 | 5.2981 | 5.3681 | 5.811 | 5.811 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.7484 | 5.7658 | 5.7918 | 5.8267 | 5.8704 | 5.8998 | 5.9293 | 5.959 | 5.9888 | 6.0188 | 6.0212 | 6.0292 | 6.0481 | 6.0778 | 6.1195 | 6.1507 | 6.1804 | 6.2083 | 6.2372 | 6.2663 | 10 | 0.48806 | 0.40939 | 0.65271 | 0.97172 | 1.325 | 0.22419 | 0.24542 | 0.31723 | 0.4812 | 0.81877 | 1.1443 | 1.5451 | 1.954 | 2.4446 | 2.977 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 10740.0576 | 11756.8582 | 15196.9675 | 23051.7953 | 39223.2341 | 54815.8802 | 74020.5323 | 93607.3403 | 117110.9325 | 142616.1916 | 0 | 0 | 4.8135 | 4.785 | 4.7879 | 4.8443 | 4.898 | 4.9719 | 5.0569 | 5.1532 | 5.2413 | 5.3268 | 0 | 0 | 5.7484 | 5.7658 | 5.7918 | 5.8267 | 5.8704 | 5.8998 | 5.9293 | 5.959 | 5.9888 | 6.0188 | 0.95215 | 0 | 4.3726 | 0 | 0 | No
FT021 Feeder | FT0-021 | Jemena | DF | 11 | 11 | Augment feeder FT0-021 | economic/probabilistic | -37.7917 | 144.9319 | -37.796013 | 144.915878 | 1207 | 0.96252 | Capacity | $401k |  |  |  | $401k | 0.3 | 0.3 | $23k | $401k |  | 47423 |  | FALSE | TRUE | FALSE | FALSE | 5.9063 | 5.9063 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.4461 | 4.6957 | 4.6985 | 4.7538 | 4.8066 | 4.9276 | 5.0617 | 5.2094 | 5.3512 | 5.4926 | 4.5123 | 4.7548 | 4.7588 | 4.8035 | 4.8578 | 4.9825 | 5.1226 | 5.2663 | 5.4092 | 5.5352 | 5.9063 | 5.9063 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.7275 | 5.1255 | 5.2372 | 5.3578 | 5.4878 | 5.6612 | 5.8387 | 6.0201 | 6.2057 | 6.3955 | 4.9518 | 5.3597 | 5.469 | 5.5888 | 5.7207 | 5.902 | 6.0859 | 6.2719 | 6.4631 | 6.6585 | 10 | 0 | 0.37668 | 0.74561 | 1.4464 | 1.8093 | 0 | 0.0018053 | 0.041069 | 0.55025 | 1.2868 | 2.4381 | 3.3404 | 4.8992 | 8.6371 | 16.5535 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 0 | 86.4832 | 1967.405 | 26359.8706 | 61644.8093 | 116799.686 | 160024.4817 | 234698.7119 | 413761.1648 | 793001.5201 | 0 | 0 | 4.4461 | 4.6957 | 4.6985 | 4.7538 | 4.8066 | 4.9276 | 5.0617 | 5.2094 | 5.3512 | 5.4926 | 0 | 0 | 4.7275 | 5.1255 | 5.2372 | 5.3578 | 5.4878 | 5.6612 | 5.8387 | 6.0201 | 6.2057 | 6.3955 | 0.95215 | 0 | 4.721 | 0 | 0 | No
FT022 Feeder | FT0-022 | Jemena | DF | 11 | 11 | Establish new feeder FT0-025 | economic/probabilistic | -37.7917 | 144.9319 | -37.784587 | 144.93859 | 1407 | 0.90774 | Capacity |  |  |  | $2.1m | $2.1m | 0.3 | 0.3 | $118k | $2.1m |  | 46327 |  | TRUE | FALSE | FALSE | FALSE | 7.1447 | 7.1447 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.753 | 4.2799 | 5.2127 | 5.8839 | 6.307 | 6.4657 | 6.6417 | 6.8356 | 7.0216 | 7.2071 | 4.9453 | 4.4431 | 5.4128 | 6.0953 | 6.5348 | 6.7026 | 6.8911 | 7.0844 | 7.2766 | 7.4461 | 7.1447 | 7.1447 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4.4955 | 4.1694 | 5.2045 | 5.9791 | 6.5363 | 6.8275 | 7.0476 | 7.2674 | 7.4814 | 7.6917 | 4.7088 | 4.3599 | 5.4347 | 6.2368 | 6.8137 | 7.1179 | 7.346 | 7.5714 | 7.7917 | 8.0081 | 10 | 0.29955 | 0.49211 | 2.7833 | 4.7642 | 5.8949 | 0.00015485 | 0.0010525 | 1.3941 | 5.5336 | 8.7391 | 9.2115 | 9.7186 | 11.0309 | 14.4856 | 22.0961 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 7.418 | 50.4201 | 66785.4259 | 265086.7032 | 418651.0009 | 441280.0553 | 465570.0509 | 528440.6781 | 693936.144 | 1058519.9609 | 0 | 0 | 4.753 | 4.2799 | 5.2127 | 5.8839 | 6.307 | 6.4657 | 6.6417 | 6.8356 | 7.0216 | 7.2071 | 0 | 0 | 4.4955 | 4.1694 | 5.2045 | 5.9791 | 6.5363 | 6.8275 | 7.0476 | 7.2674 | 7.4814 | 7.6917 | 0.95215 | 0 | 4.6307 | 0 | 0 | No
FT032 Feeder | FT0-032 | Jemena | DF | 11 | 11 | Establish new feeder FT0-025 | economic/probabilistic | -37.7917 | 144.9319 | -37.784587 | 144.93859 | 236 | 0.72615 | Capacity |  |  |  | $2.1m | $2.1m | 0.3 | 0.3 | $118k | $2.1m |  | 46328 |  | TRUE | FALSE | FALSE | FALSE | 7.1447 | 7.1447 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.3887 | 3.9503 | 5.8297 | 7.2826 | 8.102 | 8.5757 | 8.9729 | 9.2347 | 9.4861 | 9.7367 | 2.5053 | 4.1339 | 6.102 | 7.6048 | 8.4622 | 8.9612 | 9.3845 | 9.6477 | 9.9094 | 10.1403 | 7.1447 | 7.1447 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.139 | 3.6417 | 5.5081 | 7.0036 | 7.9466 | 8.5701 | 9.0107 | 9.2917 | 9.5654 | 9.8343 | 2.2405 | 3.8081 | 5.7519 | 7.3054 | 8.2838 | 8.9346 | 9.3923 | 9.6804 | 9.9621 | 10.2387 | 10 | 0 | 0 | 1.4586 | 4.3151 | 5.9298 | 0 | 0 | 0.053446 | 2.5336 | 46.6964 | 182.4395 | 385.0792 | 574.7087 | 808.4391 | 1087.2574 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 0 | 0 | 2560.3244 | 121373.8392 | 2237006.1428 | 8739815.8258 | 18447329.9265 | 27531584.5932 | 38728509.1217 | 52085379.545 | 0 | 0 | 2.3887 | 3.9503 | 5.8297 | 7.2826 | 8.102 | 8.5757 | 8.9729 | 9.2347 | 9.4861 | 9.7367 | 0 | 0 | 2.139 | 3.6417 | 5.5081 | 7.0036 | 7.9466 | 8.5701 | 9.0107 | 9.2917 | 9.5654 | 9.8343 | 0.95215 | 0 | 5.9598 | 0 | 0 | No
FT033 Feeder | FT0-033 | Jemena | DF | 11 | 11 | Establish new feeder FT-12 | economic/probabilistic | -37.7917 | 144.9319 | -37.7916 | 144.9322 | 63 | 0.67742 | Capacity |  |  |  | $1.2m | $1.2m | 0.3 | 0.3 | $68k | $1.2m |  | 47058 |  | FALSE | TRUE | FALSE | FALSE | 7.1447 | 7.1447 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.4201 | 3.9747 | 4.9133 | 5.3369 | 5.7631 | 5.9081 | 6.069 | 6.2461 | 6.4161 | 6.5856 | 3.471 | 4.0248 | 4.9763 | 5.3926 | 5.8244 | 5.974 | 6.142 | 6.3143 | 6.4856 | 6.6366 | 7.1447 | 7.1447 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 3.792 | 4.5378 | 5.7489 | 6.3559 | 6.9999 | 7.3118 | 7.5474 | 7.7828 | 8.012 | 8.2373 | 3.972 | 4.7451 | 6.0033 | 6.6299 | 7.2969 | 7.6228 | 7.867 | 8.1084 | 8.3443 | 8.576 | 10 | 0 | 0 | 1.523 | 3.5149 | 4.8002 | 0 | 0 | 0.19046 | 1.248 | 2.4985 | 4.1594 | 8.811 | 19.1411 | 38.252 | 69.4043 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 0 | 0 | 9124.0609 | 59785.4615 | 119693.0587 | 199255.1869 | 422092.2871 | 916961.8175 | 1832471.4613 | 3324834.1812 | 0 | 0 | 3.4201 | 3.9747 | 4.9133 | 5.3369 | 5.7631 | 5.9081 | 6.069 | 6.2461 | 6.4161 | 6.5856 | 0 | 0 | 3.792 | 4.5378 | 5.7489 | 6.3559 | 6.9999 | 7.3118 | 7.5474 | 7.7828 | 8.012 | 8.2373 | 0.95215 | 0 | 5.9137 | 0 | 0 | No
KLO013 Feeder | KLO-013 | Jemena | DF | 22 | 22 | New feeder KLO-023 | economic/probabilistic | -37.538324 | 144.9412 | -37.546555 | 144.885134 | 6201 | 0.98569 | Capacity |  |  |  | $1.2m | $1.2m | 0.3 | 0.3 | $68k | $1.2m |  | 46327 |  | TRUE | FALSE | FALSE | FALSE | 14.2894 | 14.2894 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10.8607 | 13.9056 | 15.0492 | 15.6179 | 15.9087 | 16.5502 | 17.252 | 18.0178 | 18.7817 | 19.5628 | 11.773 | 15.0398 | 16.2804 | 16.8558 | 17.1731 | 17.8742 | 18.6485 | 19.4549 | 20.278 | 21.0571 | 14.2894 | 14.2894 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.7614 | 11.5434 | 12.8036 | 13.5247 | 14.0509 | 14.8938 | 15.6011 | 16.3253 | 17.0545 | 17.7931 | 9.1773 | 12.0708 | 13.3701 | 14.1076 | 14.6471 | 15.5273 | 16.2617 | 17.0082 | 17.7619 | 18.5249 | 10 | 0 | 0 | 2.9415 | 3.833 | 4.2003 | 0 | 0.65382 | 6.2758 | 13.8502 | 19.5094 | 39.4418 | 73.3269 | 129.185 | 203.8001 | 301.9767 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 0 | 31321.5996 | 300646.0951 | 663499.8344 | 934605.1557 | 1889468.6385 | 3512745.559 | 6188643.5321 | 9763100.346 | 14466279.1349 | 0 | 0 | 10.8607 | 13.9056 | 15.0492 | 15.6179 | 15.9087 | 16.5502 | 17.252 | 18.0178 | 18.7817 | 19.5628 | 0 | 0 | 8.7614 | 11.5434 | 12.8036 | 13.5247 | 14.0509 | 14.8938 | 15.6011 | 16.3253 | 17.0545 | 17.7931 | 0.99375 | 0 | 22.8341 | 0 | 0 | No
KLO021 Feeder | KLO-021 | Jemena | DF | 22 | 22 | New feeder KLO-023 | economic/probabilistic | -37.538324 | 145.9412 | -37.550636 | 144.924 | 53 | 0.75714 | Capacity |  |  |  | $1.2m | $1.2m | 0.3 | 0.3 | $68k | $1.2m |  | 46327 |  | FALSE | TRUE | FALSE | FALSE | 14.2894 | 14.2894 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10.3392 | 12.8725 | 15.2973 | 17.272 | 18.4722 | 19.7731 | 20.6116 | 21.5266 | 22.4392 | 23.3724 | 11.2076 | 13.9223 | 16.5488 | 18.641 | 19.9404 | 21.355 | 22.28 | 23.2436 | 24.2269 | 25.1577 | 14.2894 | 14.2894 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11.6106 | 14.8857 | 18.1327 | 20.8393 | 22.7311 | 24.7916 | 25.9689 | 27.1744 | 28.3883 | 29.6177 | 12.1617 | 15.5658 | 18.9349 | 21.7375 | 23.6956 | 25.8461 | 27.0685 | 28.3112 | 29.5657 | 30.8357 | 10 | 8.9061 | 12.0598 | 16.4453 | 18.5245 | 19.8157 | 13.9554 | 21.3107 | 97.6308 | 356.6737 | 784.0356 | 1831.3317 | 2865.2251 | 4274.0101 | 5982.2155 | 8002.0783 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 668538.5654 | 1020896.3666 | 4677030.4046 | 17086557.4706 | 37559450.8542 | 87730474.1617 | 137259433.112 | 204747684.4391 | 286579759.4451 | 383341866.0339 | 0 | 0 | 10.3392 | 12.8725 | 15.2973 | 17.272 | 18.4722 | 19.7731 | 20.6116 | 21.5266 | 22.4392 | 23.3724 | 0 | 0 | 11.6106 | 14.8857 | 18.1327 | 20.8393 | 22.7311 | 24.7916 | 25.9689 | 27.1744 | 28.3883 | 29.6177 | 0.99375 | 0 | 2.2455 | 0 | 0 | No
SBY013 Feeder | SBY-013 | Jemena | DF | 22 | 22 | Install voltage regulator on feeder SBY-13 | economic/probabilistic | -37.5856 | 144.7222 | -37.5863 | 144.7225 | 3322 | 0.96936 | Voltage |  |  |  | $300k | $300k | 0.3 | 0.3 | $17k | $300k |  | 46327 |  | FALSE | TRUE | FALSE | FALSE | 12.5747 | 12.5747 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.6289 | 6.8656 | 7.0202 | 7.1653 | 7.2481 | 7.4146 | 7.5939 | 7.7924 | 7.9808 | 8.1674 | 7.1865 | 7.4265 | 7.5954 | 7.7341 | 7.8251 | 8.0087 | 8.2096 | 8.4149 | 8.6177 | 8.7924 | 14.0989 | 14.0989 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.7499 | 7.1995 | 7.5462 | 7.84 | 8.0886 | 8.4307 | 8.6768 | 8.9209 | 9.1565 | 9.3861 | 7.0703 | 7.5285 | 7.8801 | 8.1779 | 8.4318 | 8.7893 | 9.0442 | 9.294 | 9.5363 | 9.7721 | 10 | 0 | 0.44135 | 2.9848 | 4.7034 | 5.9117 | 0 | 0.0029774 | 8.1152 | 112.4463 | 256.3627 | 334.3202 | 369.2403 | 401.637 | 428.206 | 443.8996 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 0 | 142.6339 | 388763.0043 | 5386770.8908 | 12281131.2672 | 16015705.8944 | 17688565.2485 | 19240537.7396 | 20513332.5595 | 21265135.8796 | 0 | 0 | 6.6289 | 6.8656 | 7.0202 | 7.1653 | 7.2481 | 7.4146 | 7.5939 | 7.7924 | 7.9808 | 8.1674 | 0 | 0 | 6.7499 | 7.1995 | 7.5462 | 7.84 | 8.0886 | 8.4307 | 8.6768 | 8.9209 | 9.1565 | 9.3861 | 0.9905 | 0 | 10.6005 | 0 | 0 | No
SBY023 Feeder | SBY-023 | Jemena | DF | 22 | 22 | New feeder SBY-014 | economic/probabilistic | -37.5856 | 144.7222 | -37.586 | 144.7216 | 4044 | 0.97705 | Capacity |  |  |  | $5.6m | $5.6m | 0.3 | 0.3 | $315k | $5.6m |  | 46327 |  | TRUE | FALSE | FALSE | FALSE | 14.2894 | 14.2894 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.8858 | 10.261 | 10.5237 | 10.7243 | 10.8786 | 11.1211 | 11.3901 | 11.6878 | 11.9704 | 12.2503 | 10.6704 | 11.0506 | 11.3361 | 11.525 | 11.6931 | 11.9596 | 12.2595 | 12.5662 | 12.869 | 13.1298 | 14.2894 | 14.2894 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.4915 | 10.1456 | 10.6662 | 11.064 | 11.4468 | 11.9231 | 12.271 | 12.6163 | 12.9495 | 13.2742 | 9.942 | 10.6092 | 11.1381 | 11.5409 | 11.9325 | 12.4302 | 12.7906 | 13.144 | 13.4866 | 13.8201 | 10 | 2.7173 | 5.3156 | 6.4145 | 6.7568 | 7.0519 | 0.2305 | 3.8586 | 20.4554 | 41.5231 | 59.7605 | 71.6425 | 83.7373 | 96.9869 | 111.101 | 125.8251 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 11041.9525 | 184848.8852 | 979919.598 | 1989176.0011 | 2862844.4896 | 3432053.036 | 4011457.36 | 4646187.1299 | 5322323.7149 | 6027689.1136 | 0 | 0 | 9.8858 | 10.261 | 10.5237 | 10.7243 | 10.8786 | 11.1211 | 11.3901 | 11.6878 | 11.9704 | 12.2503 | 0 | 0 | 9.4915 | 10.1456 | 10.6662 | 11.064 | 11.4468 | 11.9231 | 12.271 | 12.6163 | 12.9495 | 13.2742 | 0.9905 | 0 | 7.927 | 0 | 0 | No
SBY024 Feeder | SBY-024 | Jemena | DF | 22 | 22 | New feeder SBY-015 | economic/probabilistic | -37.5856 | 144.7222 | -37.4757 | 144.7088 | 3845 | 0.9431 | Capacity | $4.2m |  |  |  | $4.2m | 0.3 | 0.3 | $116k | $4.2m |  | 46692 |  | TRUE | FALSE | FALSE | FALSE | 14.2894 | 14.2894 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.0089 | 10.8839 | 13.3172 | 15.0667 | 15.8373 | 16.5303 | 16.9302 | 17.3727 | 17.7928 | 18.2088 | 8.5267 | 11.5616 | 14.1498 | 15.9708 | 16.791 | 17.5343 | 17.9741 | 18.4237 | 18.8676 | 19.2501 | 14.2894 | 14.2894 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.4577 | 9.0352 | 11.3308 | 13.0478 | 13.988 | 14.8759 | 15.31 | 15.7408 | 16.1565 | 16.5616 | 6.7642 | 9.448 | 11.8321 | 13.6103 | 14.5816 | 15.5087 | 15.9583 | 16.3993 | 16.8266 | 17.2427 | 10 | 0 | 0 | 0 | 1.3619 | 2.4121 | 0 | 0 | 0 | 2.9517 | 10.0243 | 28.9841 | 52.5971 | 91.8858 | 152.6392 | 237.1928 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 0 | 0 | 0 | 141402.4545 | 480216.6283 | 1388489.9841 | 2519676.9234 | 4401814.8215 | 7312223.0987 | 11362790.3404 | 0 | 0 | 8.0089 | 10.8839 | 13.3172 | 15.0667 | 15.8373 | 16.5303 | 16.9302 | 17.3727 | 17.7928 | 18.2088 | 0 | 0 | 6.4577 | 9.0352 | 11.3308 | 13.0478 | 13.988 | 14.8759 | 15.31 | 15.7408 | 16.1565 | 16.5616 | 0.9905 | 0 | 19.2088 | 0 | 0 | No
SBY024 Feeder | SBY-024 | Jemena | DF | 22 | 22 | Augment steel section - SBY24 | economic/probabilistic | -37.5856 | 144.7222 | -37.4757 | 144.7088 | 3845 | 0.9431 | Asset Rating | $1.3m |  |  |  | $1.3m | 0.3 | 0.3 | $73k | $1.3m |  | 47423 |  | TRUE | FALSE | FALSE | FALSE | 14.2894 | 14.2894 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.0089 | 10.8839 | 13.3172 | 15.0667 | 15.8373 | 16.5303 | 16.9302 | 17.3727 | 17.7928 | 18.2088 | 8.5267 | 11.5616 | 14.1498 | 15.9708 | 16.791 | 17.5343 | 17.9741 | 18.4237 | 18.8676 | 19.2501 | 14.2894 | 14.2894 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.4577 | 9.0352 | 11.3308 | 13.0478 | 13.988 | 14.8759 | 15.31 | 15.7408 | 16.1565 | 16.5616 | 6.7642 | 9.448 | 11.8321 | 13.6103 | 14.5816 | 15.5087 | 15.9583 | 16.3993 | 16.8266 | 17.2427 | 10 | 0 | 0 | 0 | 1.3619 | 2.4121 | 0 | 0 | 0 | 2.9517 | 10.0243 | 28.9841 | 52.5971 | 91.8858 | 152.6392 | 237.1928 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 0 | 0 | 0 | 141402.4545 | 480216.6283 | 1388489.9841 | 2519676.9234 | 4401814.8215 | 7312223.0987 | 11362790.3404 | 0 | 0 | 8.0089 | 10.8839 | 13.3172 | 15.0667 | 15.8373 | 16.5303 | 16.9302 | 17.3727 | 17.7928 | 18.2088 | 0 | 0 | 6.4577 | 9.0352 | 11.3308 | 13.0478 | 13.988 | 14.8759 | 15.31 | 15.7408 | 16.1565 | 16.5616 | 0.9905 | 0 | 19.2088 | 0 | 0 | No
SHM011 Feeder | SHM-011 | Jemena | DF | 22 | 22 | New feeder SBY-022 | economic/probabilistic | -37.6761 | 144.7535 | -37.6761 | 144.7535 | 3776 | 0.96106 | Capacity |  |  |  | $1.7m | $1.7m | 0.3 | 0.3 | $96k | $1.7m |  | 46327 |  | FALSE | TRUE | FALSE | FALSE | 14.2894 | 14.2894 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.4995 | 7.7384 | 9.9566 | 11.5537 | 12.4165 | 13.0753 | 13.657 | 14.0971 | 14.5235 | 14.9513 | 5.5813 | 7.8358 | 10.0844 | 11.6744 | 12.5487 | 13.2209 | 13.8212 | 14.2509 | 14.6808 | 15.0672 | 14.2894 | 14.2894 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.5766 | 8.2987 | 11.0989 | 13.1907 | 14.4933 | 15.5653 | 16.3456 | 16.9051 | 17.4545 | 17.9983 | 5.8412 | 8.6779 | 11.59 | 13.7592 | 15.1082 | 16.2273 | 17.0378 | 17.6123 | 18.1785 | 18.7385 | 10 | 0 | 0 | 0 | 0 | 0.38705 | 0 | 0 | 0 | 0 | 1.683 | 27.2901 | 92.385 | 183.444 | 318.0995 | 496.9334 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 0 | 0 | 0 | 0 | 80626.3989 | 1307339.7605 | 4425727.9 | 8787939.8237 | 15238650.5484 | 23805736.5322 | 0 | 0 | 5.4995 | 7.7384 | 9.9566 | 11.5537 | 12.4165 | 13.0753 | 13.657 | 14.0971 | 14.5235 | 14.9513 | 0 | 0 | 5.5766 | 8.2987 | 11.0989 | 13.1907 | 14.4933 | 15.5653 | 16.3456 | 16.9051 | 17.4545 | 17.9983 | 0.98368 | 0 | 17.4232 | 0 | 0 | No
SHM014 Feeder | SHM-014 | Jemena | DF | 22 | 22 | New feeder SHM-13 | economic/probabilistic | -37.6761 | 144.7535 | -37.6761 | 144.7535 | 5148 | 0.98226 | Capacity |  |  |  | $4.5m | $4.5m | 0.3 | 0.3 | $253k | $4.5m |  | 46327 |  | TRUE | FALSE | FALSE | FALSE | 14.2894 | 14.2894 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13.6416 | 15.984 | 17.5749 | 18.8402 | 19.4464 | 20.1395 | 20.7489 | 21.4175 | 22.0654 | 22.7152 | 14.6368 | 17.1115 | 18.819 | 20.1263 | 20.7781 | 21.529 | 22.1999 | 22.8901 | 23.5806 | 24.2013 | 14.2894 | 14.2894 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.9726 | 10.8383 | 12.2224 | 13.3407 | 14.0456 | 14.8216 | 15.3446 | 15.8698 | 16.3856 | 16.896 | 9.3985 | 11.3335 | 12.7632 | 13.9157 | 14.6416 | 15.4521 | 15.9943 | 16.5337 | 17.0652 | 17.5909 | 10 | 0 | 2.5769 | 6.3539 | 9.6243 | 11.5455 | 0.21111 | 10.176 | 29.1584 | 58.5483 | 81.7015 | 119.5955 | 165.4228 | 233.8056 | 332.0341 | 466.1018 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 10113.2155 | 487485.9746 | 1396840.1483 | 2804772.9495 | 3913934.1134 | 5729255.9405 | 7924627.6779 | 11200522.7825 | 15906189.6029 | 22328739.9066 | 0 | 0 | 13.6416 | 15.984 | 17.5749 | 18.8402 | 19.4464 | 20.1395 | 20.7489 | 21.4175 | 22.0654 | 22.7152 | 0 | 0 | 8.9726 | 10.8383 | 12.2224 | 13.3407 | 14.0456 | 14.8216 | 15.3446 | 15.8698 | 16.3856 | 16.896 | 0.98368 | 0 | 16.9903 | 0 | 0 | No
ST011 Feeder | ST0-011 | Jemena | DF | 22 | 22 | Establish CBN Zone Substation | economic/probabilistic | -37.6225 | 144.9486 | -37.6224 | 144.9485 | 3574 | 0.91688 | Capacity |  |  |  | $34.0m | $34.0m | 0.3 | 0.3 | $1.9m | $34.0m |  | 46692 |  | FALSE | TRUE | FALSE | FALSE | 22.482 | 22.482 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13.7005 | 14.4372 | 15.3534 | 15.7768 | 15.9914 | 16.4747 | 17.0065 | 17.589 | 18.1568 | 18.7282 | 13.9044 | 14.6191 | 15.5504 | 15.9416 | 16.1617 | 16.6582 | 17.211 | 17.781 | 18.3534 | 18.8735 | 22.482 | 22.482 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16.4869 | 17.8347 | 19.3662 | 20.1209 | 20.6602 | 21.4182 | 22.1982 | 23.0008 | 23.8267 | 24.6764 | 17.2695 | 18.6496 | 20.2231 | 20.9882 | 21.5369 | 22.3292 | 23.1381 | 23.963 | 24.8149 | 25.6912 | 10 | 0 | 0 | 4.709 | 8.0644 | 10.0774 | 0 | 0.085167 | 17.0338 | 57.2926 | 84.6731 | 103.3539 | 123.9825 | 141.3716 | 186.6482 | 304.8479 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 0 | 4079.9501 | 816010.2621 | 2744620.7582 | 4056288.8603 | 4951196.1497 | 5939415.5606 | 6772445.432 | 8941433.6253 | 14603824.9809 | 0 | 0 | 13.7005 | 14.4372 | 15.3534 | 15.7768 | 15.9914 | 16.4747 | 17.0065 | 17.589 | 18.1568 | 18.7282 | 0 | 0 | 16.4869 | 17.8347 | 19.3662 | 20.1209 | 20.6602 | 21.4182 | 22.1982 | 23.0008 | 23.8267 | 24.6764 | 0.96151 | 0 | 20.8862 | 0 | 0 | No
ST022 Feeder | ST0-022 | Jemena | DF | 22 | 22 | Establish CBN Zone Substation | economic/probabilistic | -37.6225 | 144.9486 | -37.6225 | 144.9485 | 2835 | 0.91599 | Capacity |  |  |  | $34.0m | $34.0m | 0.3 | 0.3 | $1.9m | $34.0m |  | 46693 |  | FALSE | TRUE | FALSE | FALSE | 22.482 | 22.482 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13.9865 | 16.9972 | 19.9354 | 22.2325 | 23.8282 | 24.789 | 25.8402 | 26.9873 | 28.1314 | 29.3013 | 14.5515 | 17.6441 | 20.6991 | 23.0297 | 24.6875 | 25.6955 | 26.8086 | 27.9679 | 29.1512 | 30.2711 | 22.482 | 22.482 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 14.3856 | 17.9396 | 21.4797 | 24.2168 | 26.2907 | 27.5224 | 28.8043 | 30.1384 | 31.5267 | 32.9711 | 15.0684 | 18.7593 | 22.43 | 25.2606 | 27.4062 | 28.693 | 30.024 | 31.3992 | 32.8343 | 34.3271 | 10 | 0 | 1.7336 | 7.5943 | 11.3649 | 13.8102 | 0 | 0.5866 | 24.5547 | 143.9227 | 781.3607 | 1571.9135 | 2753.9442 | 4349.0966 | 6369.5817 | 8798.8829 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 0 | 28101.2595 | 1176301.1187 | 6894660.6775 | 37431308.706 | 75302968.7326 | 131928492.5696 | 208344724.7597 | 305136648.5323 | 421513020.1662 | 0 | 0 | 13.9865 | 16.9972 | 19.9354 | 22.2325 | 23.8282 | 24.789 | 25.8402 | 26.9873 | 28.1314 | 29.3013 | 0 | 0 | 14.3856 | 17.9396 | 21.4797 | 24.2168 | 26.2907 | 27.5224 | 28.8043 | 30.1384 | 31.5267 | 32.9711 | 0.96151 | 0 | 20.2098 | 0 | 0 | No
ST033 Feeder | ST0-033 | Jemena | DF | 22 | 22 | Establish CBN Zone Substation | economic/probabilistic | -37.6225 | 144.9486 | -37.6226 | 144.9485 | 3645 | 0.97019 | Capacity |  |  |  | $34.0m | $34.0m | 0.3 | 0.3 | $1.9m | $34.0m |  | 46694 |  | TRUE | FALSE | FALSE | FALSE | 12.0031 | 12.0031 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.1881 | 9.2123 | 9.2696 | 9.3602 | 9.4405 | 9.6305 | 9.8439 | 10.0813 | 10.3047 | 10.5248 | 9.9018 | 9.9056 | 9.9696 | 10.0433 | 10.1315 | 10.3404 | 10.5788 | 10.822 | 11.0609 | 11.2628 | 12.0031 | 12.0031 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.5578 | 8.809 | 9.0516 | 9.2416 | 9.4423 | 9.6927 | 9.9472 | 10.2058 | 10.4686 | 10.7357 | 8.964 | 9.2115 | 9.452 | 9.6399 | 9.8429 | 10.105 | 10.3684 | 10.6328 | 10.9028 | 11.1772 | 10 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.00070766 | 0.0085052 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 8760 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33.9006 | 407.4459 | 0 | 0 | 9.1881 | 9.2123 | 9.2696 | 9.3602 | 9.4405 | 9.6305 | 9.8439 | 10.0813 | 10.3047 | 10.5248 | 0 | 0 | 8.5578 | 8.809 | 9.0516 | 9.2416 | 9.4423 | 9.6927 | 9.9472 | 10.2058 | 10.4686 | 10.7357 | 0.96151 | 0 | 30.7729 | 0 | 0 | No
TT011 Feeder | TT0-011 | Jemena | DF | 22 | 22 | Augment feeder TT0-011 | economic/probabilistic | -37.6923 | 145.0086 | -37.6909 | 145.0108 | 5564 | 0.9801 | Capacity | $1.7m |  |  |  | $1.7m | 0.3 | 0.3 | $96k | $1.7m |  | 47058 |  | TRUE | FALSE | FALSE | FALSE | 12.3842 | 12.3842 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.3194 | 6.3169 | 6.3648 | 6.4617 | 6.5009 | 6.5989 | 6.7118 | 6.8396 | 6.9565 | 7.0699 | 6.9026 | 6.8843 | 6.9381 | 7.0272 | 7.0712 | 7.1813 | 7.3105 | 7.4416 | 7.5681 | 7.6682 | 12.3842 | 12.3842 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6.742 | 6.9189 | 7.1191 | 7.3077 | 7.4479 | 7.6076 | 7.7687 | 7.9312 | 8.0951 | 8.2605 | 7.062 | 7.2351 | 7.4341 | 7.6227 | 7.7639 | 7.9311 | 8.0976 | 8.263 | 8.4309 | 8.6002 | 10 | 6.9026 | 6.8843 | 6.9381 | 7.0272 | 7.0712 | 0.0095834 | 0.060446 | 0.20984 | 0.38997 | 0.58195 | 0.88795 | 1.4513 | 2.0738 | 2.8272 | 3.6786 | 8756 | 8756 | 8756 | 8756 | 8756 | 8756 | 8756 | 8756 | 8756 | 8756 | 459.0953 | 2895.7003 | 10052.2218 | 18681.8158 | 27878.4779 | 42537.3274 | 69526.2422 | 99345.903 | 135439.0261 | 176223.1161 | 0 | 0 | 4.0775 | 4.8301 | 5.3677 | 5.3786 | 5.4347 | 5.5574 | 5.7042 | 5.863 | 6.0283 | 6.1845 | 0 | 0 | 3.9953 | 4.8754 | 5.5641 | 5.6711 | 5.7814 | 5.9069 | 6.0335 | 6.1613 | 6.2902 | 6.4202 | 0.98509 | 0 | 6.0782 | 0 | 0 | No
BTS-FF-BTS | BTS-FF181 | Jemena | STL | 22 | 22 | Augment BTS-FF 22kV Loop - Sub Transmission Works | economic/probabilistic | -37.7729 | 144.9848 | -37.7699 | 145.0202 | 6337 | 0.92484 | Capacity | $0 (Committed Project) |  |  |  | $0 (Committed Project) | 0.3 | 0.3 | $0 (Committed Project) | $0 (Committed Project) |  | 46327 |  | TRUE | FALSE | FALSE | FALSE | 11.4 | 11.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 6 | 6.2 | 6.8 | 7.4 | 7.8 | 8.1 | 8.4 | 8.6 | 8.8 | 9 | 6.4 | 6.6 | 7.2 | 7.8 | 8.3 | 8.6 | 8.9 | 9.1 | 9.4 | 9.6 | 13 | 13 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5.3 | 5.6 | 6.3 | 7 | 7.6 | 8 | 8.2 | 8.5 | 8.7 | 9 | 5.6 | 5.9 | 6.6 | 7.3 | 7.9 | 8.3 | 8.6 | 8.9 | 9.1 | 9.4 | 10 | 3.7872 | 4.2855 | 5.9797 | 7.5743 | 8.8699 | 0.83452 | 3.272 | 25.9014 | 101.5082 | 206.6653 | 301.9781 | 416.4017 | 528.2309 | 626.4561 | 754.7053 | 44.5 | 61.5 | 100.5 | 128.5 | 165 | 169 | 211.5 | 235 | 268 | 323 | 39977.8144 | 156745.9803 | 1240807.0687 | 4862751.2667 | 9900299.8613 | 14466259.6713 | 19947721.1893 | 25304903.5202 | 30010380.8514 | 36154159.4023 | 0 | 0 | 3.8 | 4.3 | 6 | 7.6 | 8.9 | 9.8 | 10.6 | 11.2 | 11.8 | 12.4 | 0 | 0 | 0.9 | 1.8 | 3.8 | 5.6 | 7.1 | 8.3 | 9 | 9.8 | 10.5 | 11.2 | 0.99662 |  |  | 0 | 0 | No
BTS-FF-BTS | BTS-FF184 | Jemena | STL | 22 | 22 | Augment BTS-FF 22kV Loop - Sub Transmission Works | economic/probabilistic | -37.7729 | 144.9848 | -37.7699 | 145.0202 | 6337 | 0.92484 | Capacity | $0 (Committed Project) |  |  |  | $0 (Committed Project) | 0.3 | 0.3 | $0 (Committed Project) | $0 (Committed Project) |  | 46327 |  | TRUE | FALSE | FALSE | FALSE | 13.1 | 13.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.5 | 9.8 | 10.7 | 11.6 | 12.3 | 12.8 | 13.2 | 13.5 | 13.9 | 14.2 | 10.1 | 10.4 | 11.4 | 12.3 | 13.1 | 13.6 | 14.1 | 14.4 | 14.8 | 15.1 | 13.7 | 13.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.4 | 8.9 | 10 | 11.1 | 11.9 | 12.6 | 12.9 | 13.4 | 13.7 | 14.1 | 8.8 | 9.3 | 10.5 | 11.6 | 12.4 | 13.1 | 13.5 | 14 | 14.4 | 14.8 | 10 | 3.7872 | 4.2855 | 5.9797 | 7.5743 | 8.8699 | 0.83452 | 3.272 | 25.9014 | 101.5082 | 206.6653 | 301.9781 | 416.4017 | 528.2309 | 626.4561 | 754.7053 | 44.5 | 61.5 | 100.5 | 128.5 | 165 | 169 | 211.5 | 235 | 268 | 323 | 39977.8144 | 156745.9803 | 1240807.0687 | 4862751.2667 | 9900299.8613 | 14466259.6713 | 19947721.1893 | 25304903.5202 | 30010380.8514 | 36154159.4023 | 0 | 0 | 3.8 | 4.3 | 6 | 7.6 | 8.9 | 9.8 | 10.6 | 11.2 | 11.8 | 12.4 | 0 | 0 | 0.9 | 1.8 | 3.8 | 5.6 | 7.1 | 8.3 | 9 | 9.8 | 10.5 | 11.2 | 0.99662 |  |  | 0 | 0 | No
BTS-FF-BTS | BTS-FF188 | Jemena | STL | 22 | 22 | Augment BTS-FF 22kV Loop - Sub Transmission Works | economic/probabilistic | -37.7729 | 144.9848 | -37.7699 | 145.0202 | 6337 | 0.92484 | Capacity | $0 (Committed Project) |  |  |  | $0 (Committed Project) | 0.3 | 0.3 | $0 (Committed Project) | $0 (Committed Project) |  | 46327 |  | TRUE | FALSE | FALSE | FALSE | 13.1 | 13.1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.8 | 10.1 | 11 | 11.9 | 12.6 | 13.1 | 13.5 | 13.9 | 14.3 | 14.6 | 10.4 | 10.7 | 11.7 | 12.7 | 13.4 | 14 | 14.4 | 14.8 | 15.2 | 15.5 | 13.7 | 13.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8.6 | 9.1 | 10.3 | 11.4 | 12.2 | 12.9 | 13.3 | 13.7 | 14.1 | 14.5 | 9 | 9.6 | 10.7 | 11.9 | 12.8 | 13.5 | 13.9 | 14.4 | 14.8 | 15.2 | 10 | 3.7872 | 4.2855 | 5.9797 | 7.5743 | 8.8699 | 0.83452 | 3.272 | 25.9014 | 101.5082 | 206.6653 | 301.9781 | 416.4017 | 528.2309 | 626.4561 | 754.7053 | 44.5 | 61.5 | 100.5 | 128.5 | 165 | 169 | 211.5 | 235 | 268 | 323 | 39977.8144 | 156745.9803 | 1240807.0687 | 4862751.2667 | 9900299.8613 | 14466259.6713 | 19947721.1893 | 25304903.5202 | 30010380.8514 | 36154159.4023 | 0 | 0 | 3.8 | 4.3 | 6 | 7.6 | 8.9 | 9.8 | 10.6 | 11.2 | 11.8 | 12.4 | 0 | 0 | 0.9 | 1.8 | 3.8 | 5.6 | 7.1 | 8.3 | 9 | 9.8 | 10.5 | 11.2 | 0.99662 |  |  | 0 | 0 | No
BTS-NS-BTS | BTS-NS176 | Jemena | STL | 22 | 22 | Augment BTS-NS 22kV loop | economic/probabilistic | -37.7729 | 144.9848 | -37.7512 | 144.929 | 10471 | 0.89236 | Capacity | $2.5m |  |  |  | $2.5m | 0.3 | 0.3 | $0.142m | $2.5m |  | 47423 |  | TRUE | FALSE | FALSE | FALSE | 15.2 | 15.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 13.1 | 13.6 | 14.3 | 14.8 | 15.3 | 15.9 | 16.4 | 16.9 | 17.3 | 14.8 | 14.9 | 15.5 | 16.3 | 16.9 | 17.5 | 18.1 | 18.7 | 19.2 | 19.8 | 15.2 | 15.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10.1 | 10.6 | 11.2 | 11.9 | 12.6 | 13.1 | 13.5 | 14 | 14.4 | 14.8 | 10.7 | 11.1 | 11.7 | 12.5 | 13.1 | 13.7 | 14.1 | 14.6 | 15 | 15.5 | 10 | 8.2614 | 8.5463 | 9.4959 | 10.6354 | 11.8699 | 51.875 | 52.4682 | 85.9898 | 144.6496 | 209.5677 | 268.0054 | 390.2425 | 499.3269 | 620.8536 | 718.2548 | 68.5 | 78.5 | 101 | 108 | 128 | 168 | 175.5 | 205.5 | 240.5 | 280.5 | 2485071.7037 | 2513488.6417 | 4119339.48 | 6929438.9314 | 10039339.724 | 12838800.4871 | 18694567.8761 | 23920254.3069 | 29741990.4463 | 34407996.9582 | 0 | 0 | 8.7 | 9 | 10 | 11.2 | 12.5 | 13.5 | 14.9 | 16 | 17 | 18.2 | 0 | 0 | 1.4 | 2.1 | 3.2 | 4.4 | 5.6 | 6.4 | 7.3 | 8 | 8.7 | 9.6 | 0.94959 |  |  | 0 | 0 | No
BTS-NS-BTS | BTS-NS190 | Jemena | STL | 22 | 22 | Augment BTS-NS 22kV loop | economic/probabilistic | -37.7729 | 144.9848 | -37.7512 | 144.929 | 10471 | 0.89236 | Capacity | $2.5m |  |  |  | $2.5m | 0.3 | 0.3 | $0.142m | $2.5m |  | 47424 |  | TRUE | FALSE | FALSE | FALSE | 15.2 | 15.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12.6 | 12.8 | 13.2 | 13.9 | 14.4 | 14.8 | 15.4 | 15.9 | 16.4 | 16.9 | 14.4 | 14.5 | 15.1 | 15.8 | 16.4 | 17 | 17.6 | 18.2 | 18.7 | 19.2 | 15.2 | 15.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 9.9 | 10.3 | 10.9 | 11.6 | 12.2 | 12.7 | 13.2 | 13.6 | 14 | 14.4 | 10.4 | 10.8 | 11.4 | 12.2 | 12.8 | 13.3 | 13.7 | 14.2 | 14.6 | 15 | 10 | 8.2614 | 8.5463 | 9.4959 | 10.6354 | 11.8699 | 51.875 | 52.4682 | 85.9898 | 144.6496 | 209.5677 | 268.0054 | 390.2425 | 499.3269 | 620.8536 | 718.2548 | 68.5 | 78.5 | 101 | 108 | 128 | 168 | 175.5 | 205.5 | 240.5 | 280.5 | 2485071.7037 | 2513488.6417 | 4119339.48 | 6929438.9314 | 10039339.724 | 12838800.4871 | 18694567.8761 | 23920254.3069 | 29741990.4463 | 34407996.9582 | 0 | 0 | 8.7 | 9 | 10 | 11.2 | 12.5 | 13.5 | 14.9 | 16 | 17 | 18.2 | 0 | 0 | 1.4 | 2.1 | 3.2 | 4.4 | 5.6 | 6.4 | 7.3 | 8 | 8.7 | 9.6 | 0.94959 |  |  | 0 | 0 | No
BTS-NS-BTS | BTS-NS193 | Jemena | STL | 22 | 22 | Augment BTS-NS 22kV loop | economic/probabilistic | -37.7729 | 144.9848 | -37.7512 | 144.929 | 10471 | 0.89236 | Capacity | $2.5m |  |  |  | $2.5m | 0.3 | 0.3 | $0.142m | $2.5m |  | 47425 |  | TRUE | FALSE | FALSE | FALSE | 15.2 | 15.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 13 | 13.2 | 13.7 | 14.3 | 14.9 | 15.4 | 15.9 | 16.4 | 16.9 | 17.4 | 14.9 | 15 | 15.6 | 16.3 | 17 | 17.5 | 18.2 | 18.8 | 19.3 | 19.9 | 21.9 | 21.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 10.2 | 10.6 | 11.3 | 12 | 12.6 | 13.1 | 13.6 | 14 | 14.4 | 14.9 | 10.7 | 11.1 | 11.8 | 12.6 | 13.2 | 13.7 | 14.2 | 14.7 | 15.1 | 15.5 | 10 | 8.2614 | 8.5463 | 9.4959 | 10.6354 | 11.8699 | 51.875 | 52.4682 | 85.9898 | 144.6496 | 209.5677 | 268.0054 | 390.2425 | 499.3269 | 620.8536 | 718.2548 | 68.5 | 78.5 | 101 | 108 | 128 | 168 | 175.5 | 205.5 | 240.5 | 280.5 | 2485071.7037 | 2513488.6417 | 4119339.48 | 6929438.9314 | 10039339.724 | 12838800.4871 | 18694567.8761 | 23920254.3069 | 29741990.4463 | 34407996.9582 | 0 | 0 | 8.7 | 9 | 10 | 11.2 | 12.5 | 13.5 | 14.9 | 16 | 17 | 18.2 | 0 | 0 | 1.4 | 2.1 | 3.2 | 4.4 | 5.6 | 6.4 | 7.3 | 8 | 8.7 | 9.6 | 0.94959 |  |  | 0 | 0 | No
KTS-AW-PV-KTS | KTS-AW1 | Jemena | STL | 66 | 66 | Augment KTS-AW | economic/probabilistic | -37.739576 | 144.8447 | -37.715103 | 144.886369 | 41928 | 0.91889 | Capacity | $5.0m |  |  |  | $5.0m | 0.3 | 0.3 | $0.281m | $5.0m |  | 46327 |  | TRUE | FALSE | FALSE | FALSE | 117 | 117 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31.3 | 34.5 | 37.9 | 41.3 | 44.1 | 47.3 | 50.5 | 53.9 | 57.2 | 57.7 | 29.4 | 39.5 | 44.9 | 50.5 | 55.6 | 61 | 66.5 | 71.9 | 72.4 | 72.9 | 126 | 126 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25.5 | 28.7 | 32 | 35.1 | 37.8 | 40.6 | 43.3 | 46.1 | 48.8 | 49.2 | 23.4 | 33.4 | 39.2 | 44.8 | 50.1 | 55.4 | 60.8 | 66.1 | 66.5 | 66.9 | 10 | 0 | 0 | 0 | 0 | 6.7908 | 0 | 0 | 0 | 0 | 0.00058368 | 0.0051545 | 0.34355 | 4.3505 | 7.5504 | 9.3691 | 0 | 0 | 0 | 0 | 2 | 12 | 28 | 61.5 | 64 | 68 | 0 | 0 | 0 | 0 | 27.9611 | 246.9272 | 16457.7319 | 208413.8722 | 361702.3275 | 448829.5128 | 0 | 0 | 0 | 0 | 0 | 0 | 6.8 | 15.7 | 25 | 34.1 | 35.7 | 36.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 8.9 | 10.2 | 11.4 | 0.99865 |  |  | 0 | 0 | No
KTS-AW-PV-KTS | KTS-PV | Jemena | STL | 66 | 66 | Augment KTS-AW | economic/probabilistic | -37.739576 | 144.8447 | -37.722359 | 144.9328 | 41928 | 0.91889 | Capacity | $5.0m |  |  |  | $5.0m | 0.3 | 0.3 | $0.281m | $5.0m |  | 46328 |  | TRUE | FALSE | FALSE | FALSE | 100.6 | 100.6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 28.1 | 29.1 | 30.1 | 31.3 | 32.1 | 33.1 | 34.1 | 35.3 | 36.3 | 36.8 | 29.8 | 32.3 | 33.8 | 35.5 | 36.8 | 38.3 | 39.9 | 41.5 | 42 | 42.4 | 105.7 | 105.7 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 23.8 | 25.1 | 26.5 | 27.8 | 28.8 | 29.8 | 30.7 | 31.6 | 32.5 | 33 | 24.1 | 26.9 | 28.9 | 30.7 | 32.3 | 33.8 | 35.3 | 36.8 | 37.2 | 37.7 | 10 | 0 | 0 | 0 | 0 | 6.7908 | 0 | 0 | 0 | 0 | 0.00058368 | 0.0051545 | 0.34355 | 4.3505 | 7.5504 | 9.3691 | 0 | 0 | 0 | 0 | 2 | 12 | 28 | 61.5 | 64 | 68 | 0 | 0 | 0 | 0 | 27.9611 | 246.9272 | 16457.7319 | 208413.8722 | 361702.3275 | 448829.5128 | 0 | 0 | 0 | 0 | 0 | 0 | 6.8 | 15.7 | 25 | 34.1 | 35.7 | 36.9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.2 | 8.9 | 10.2 | 11.4 | 0.99865 |  |  | 0 | 0 | No
TTS-NEI-NH-NEL-WT-TTS | TTS-NEI/NH | Jemena | STL | 66 | 66 | Augment TTS-NEI-NH-NEL-WT-TTS 66kV loop | economic/probabilistic | -37.692079 | 145.0118 | -37.73217 | 145.0429 | 15476 | 0.95714 | Capacity | $12.4m |  |  |  | $12.4m | 0.3 | 0.3 | $0.70m | $12.4m |  | 46692 |  | TRUE | FALSE | FALSE | FALSE | 117.2 | 117.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 75.8 | 78.6 | 79.7 | 80.8 | 81.7 | 82.9 | 86.7 | 88.1 | 89.4 | 90.7 | 78.7 | 78.5 | 85.5 | 86.6 | 87.5 | 88.7 | 90.2 | 94.2 | 95.6 | 96.9 | 126.3 | 126.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 61.4 | 65.3 | 67.4 | 69 | 70.4 | 71.7 | 75.6 | 77 | 78.5 | 80 | 61.9 | 63 | 70.5 | 72 | 73.4 | 74.8 | 76.3 | 80.3 | 81.7 | 83.3 | 10 | 15.2813 | 16.1743 | 28.181 | 30.6618 | 32.1502 | 0.017578 | 0.048948 | 1.4539 | 4.0426 | 8.5658 | 10.0628 | 27.9603 | 70.9685 | 85.6253 | 108.0362 | 14.5 | 15.5 | 46.5 | 58 | 62.5 | 66 | 73.5 | 102.5 | 115.5 | 132 | 842.0682 | 2344.8383 | 69650.1119 | 193662.6155 | 410346.2043 | 482059.2521 | 1339437.8241 | 3399745.2319 | 4101879.6097 | 5175475.2471 | 0 | 0 | 15.4 | 16.3 | 28.4 | 30.9 | 32.4 | 34.8 | 37.1 | 44.4 | 47.4 | 49.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.3 | 9.3 | 12.1 | 14.9 | 0.99229 |  |  | 0 | 0 | No
TTS-NEI-NH-NEL-WT-TTS | TTS-WT | Jemena | STL | 66 | 66 | Augment TTS-NEI-NH-NEL-WT-TTS 66kV loop | economic/probabilistic | -37.692079 | 145.0118 | -37.713592 | 145.0856 | 15476 | 0.95714 | Capacity | $12.4m |  |  |  | $12.4m | 0.3 | 0.3 | $0.70m | $12.4m |  | 46693 |  | TRUE | FALSE | FALSE | FALSE | 117.2 | 117.2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 50.2 | 53.2 | 53.8 | 54.5 | 55.1 | 55.9 | 58.5 | 59.4 | 60.2 | 61.1 | 52.1 | 53.2 | 57.7 | 58.4 | 59.2 | 60 | 60.9 | 63.6 | 64.5 | 65.4 | 126.3 | 126.3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 40.2 | 43.7 | 45 | 46 | 46.9 | 47.8 | 50.5 | 51.5 | 52.5 | 53.6 | 40.5 | 42.2 | 47.1 | 48.1 | 49 | 50 | 51 | 53.7 | 54.7 | 55.8 | 10 | 15.2813 | 16.1743 | 28.181 | 30.6618 | 32.1502 | 0.017578 | 0.048948 | 1.4539 | 4.0426 | 8.5658 | 10.0628 | 27.9603 | 70.9685 | 85.6253 | 108.0362 | 14.5 | 15.5 | 46.5 | 58 | 62.5 | 66 | 73.5 | 102.5 | 115.5 | 132 | 842.0682 | 2344.8383 | 69650.1119 | 193662.6155 | 410346.2043 | 482059.2521 | 1339437.8241 | 3399745.2319 | 4101879.6097 | 5175475.2471 | 0 | 0 | 15.4 | 16.3 | 28.4 | 30.9 | 32.4 | 34.8 | 37.1 | 44.4 | 47.4 | 49.4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2.3 | 9.3 | 12.1 | 14.9 | 0.99229 |  |  | 0 | 0 | No
Note on A1: Full asset name (or, for TNSPs, 'Project Name' if more relevant). Should include any spatially represented asset type for which you wish to present data. Must match NOM polygon files. Units/format: Free text field
Note on B1: AER Ref: DT004 'shorthand' code or asset ID of Network Asset. Should be consistent with RIN Sustained Interruptions sheet from Category Analysis template. Must match NOM polygon files. Units/format: Free text field but ideally short notation no spaces and be unique.
Note on C1: Name of NSP or planning manager (for Vic transmission). Units/format: Text (drop down list)
Note on D1: AER Ref: DT005 TL: Transmission Line TS: Transmission terminal station TCP: Transmission Connection Point ZS: Zone Substation DF: (Distribution) feeder Units/format: Defined code above (drop down list)
Note on E1: AER Ref: DT009 Highest operational voltage level of the assets involved in the constraints Units/format: kV (integer)
Note on F1: AER Ref: DT009 Operational voltage level of the assets involved in the constraints on the low side of the transformer Units/format: kV (integer)
Note on G1: AER Ref: DT012 Description of the problem or general asset situation and proposed network solution. Units/format: Free text field
Note on H1: Indicate the reliability criteria applied to the network asset. For example n, n-1, n-2, n-1 + risk. Unit/Format: Free text.
Note on I1: AER Ref: DT002 Asset coordinates (starting point). Use approximate start of line for line assets. NB: These will not be mapped or made publicly accessible if 'Polygon Centre' is selected in the universal inputs sheet. Units/format: Decimal degrees
Note on J1: AER Ref: DT002 Asset coordinates (starting point). Use approximate start of line for line assets. NB: These will not be mapped or made publicly accessible if 'Polygon Centre' is selected in the universal inputs sheet. Units/format: Decimal degrees
Note on K1: AER Ref: DT003 Asset coordinates (ending point). Use approximate end of line for line assets. For substations this data would not differ from starting point. NB: These will not be mapped or made publicly accessible if 'Polygon Centre' is selected in the universal inputs sheet. Units/format: Decimal degrees
Note on L1: AER Ref: DT003 Asset coordinates (ending point). Use approximate end of line for line assets. For substations this data would not differ from starting point. NB: These will not be mapped or made publicly accessible if 'Polygon Centre' is selected in the universal inputs sheet. Units/format: Decimal degrees
Note on M1: AER Ref: DT006 Total number of customers affected
Note on N1: AER Ref: DT006_a Percent of customers affected Format: Percent, entered as a positive decimal between 0 and 1 (e.g. 15% would be entered as 0.15)
Note on O1: AER Ref: DT001 Constraint primary investment driver Format: Choose one of: capacity; reliability; asset condition; performance; safety; environment; power quality; voltage
Note on P1: Investment driver: augmentation. Provide estimated value of proposed network investment for each network asset. If zero leave blank. Demand growth related. Units/Formats: $ AUD (real)
Note on Q1: Investment driver: Replacement. Provide estimated value of proposed network investment for each network asset. If zero leave blank. Age/condition related. Units/Formats: $ AUD (real)
Note on R1: Investment driver: Connections. Provide estimated value of proposed network investment for each network asset. If zero leave blank. Units/Formats: $ AUD (real)
Note on S1: For any other investment provide estimated value of proposed network investment for each network asset. If zero leave blank. Units/Formats: $ AUD (real)
Note on T1: AER Ref: DT013 Total value of proposed network solution - should be the sum of Cols P to S (all investment types). If zero leave blank. Units/Formats: $ AUD (real)
Note on U1: AER Ref: DT014_a Format: Percent, entered as a decimal between -1 and +1. (e.g. an accuracy of +/- 15% would be entered as -0.15 in minus field 0.15 in plus field)
Note on V1: AER Ref: DT014_b Format: Percent, entered as a decimal between -1 and +1. (e.g. an accuracy of +/- 15% would be entered as -0.15 in minus field 0.15 in plus field)
Note on W1: AER Ref: DT017 Saving in cost of capital from defering the project. Note that this does not use Value of Customer Reliability as an Input, as originally specified in AER guidance. Units: $/a (real) NB: This is not the same calculation as represented in the Annual Deferral Value (ADV) map on the NOM.
Note on X1: Provide the component of the total proposed investment (Col T) that is considered deferrable with the non-network alternative/ Includes: • Defering augmentation (reducing project demand growth) • Defering new infrastructure riven by revised reliability criteria • Retiring assets (by reducing demand) • Downsizing assets (by reducing demand) • Extending the life of assets (by reducing the load conditions) Units/Formats: $ AUD (real)
Note on Y1: AER Ref: DT013_a Annual operating costs (including overheads, risk allowance and contingency allowance if included) Units/Formats: $ AUD (real)
Note on Z1: AER Ref: DT015 Provide the expected month and year when investment is planned for commissioning. Units/Format: MM/YYYY
Note on AA1: Provide the expected month and year when investment decision is locked in and non-network solutions are no longer an option. Units/Format: MM/YYYY
Note on AB1: Answer true if this season is expected to drive forecast constraints. Unit/Format: 'true' or 'false'
Note on AC1: Answer true if this season is expected to drive forecast constraints. Unit/Format: 'true' or 'false'
Note on AD1: Answer true if this season is expected to drive forecast constraints. Unit/Format: 'true' or 'false'
Note on AE1: Answer true if this season is expected to drive forecast constraints. Unit/Format: 'true' or 'false'
Note on AF1: Provide current seasonal nameplate capacity of the network asset. Units/Format: MVA
Note on AG1: Provide the current seasonal secure capacity of the network asset. Note: Some NSPs refer to this as firm capacity. Units/Format: MVA
Note on AH1: AER Ref: DT007/ DT007_a/ DT021/ DT021_a HISTORICAL SERIES (FROM CURRENT BACK 3YRS): Provide maximum seasonal capacity to operate the network (secure, nameplate capacity etc., retirement, downsizing) This specifies the level of support required from non-network service provider. Note: Do not increase accepted capacity if augmentation planned. Unit/Format: MVA
Note on AI1: AER Ref: DT007/ DT007_a/ DT021/ DT021_a HISTORICAL SERIES (FROM CURRENT BACK 3YRS): Provide maximum seasonal capacity to operate the network (secure, nameplate capacity etc., retirement, downsizing) This specifies the level of support required from non-network service provider. Note: Do not increase accepted capacity if augmentation planned. Unit/Format: MVA
Note on AJ1: AER Ref: DT007/ DT007_a/ DT021/ DT021_a HISTORICAL SERIES (FROM CURRENT BACK 3YRS): Provide maximum seasonal capacity to operate the network (secure, nameplate capacity etc., retirement, downsizing) This specifies the level of support required from non-network service provider. Note: Do not increase accepted capacity if augmentation planned. Unit/Format: MVA
Note on AK1: AER Ref: DT007/ DT007_a/ DT021/ DT021_a HISTORICAL SERIES (FROM CURRENT BACK 3YRS): Provide maximum seasonal capacity to operate the network (secure, nameplate capacity etc., retirement, downsizing) This specifies the level of support required from non-network service provider. Note: Do not increase accepted capacity if augmentation planned. Unit/Format: MVA
Note on AL1: AER Ref: DT007/ DT007_a/ DT021/ DT021_a HISTORICAL SERIES (FROM CURRENT BACK 3YRS): Provide maximum seasonal capacity to operate the network (secure, nameplate capacity etc., retirement, downsizing) This specifies the level of support required from non-network service provider. Note: Do not increase accepted capacity if augmentation planned. Unit/Format: MVA
Note on AM1: AER Ref: DT007/ DT007_a/ DT021/ DT021_a HISTORICAL SERIES (FROM CURRENT BACK 3YRS): Provide maximum seasonal capacity to operate the network (secure, nameplate capacity etc., retirement, downsizing) This specifies the level of support required from non-network service provider. Note: Do not increase accepted capacity if augmentation planned. Unit/Format: MVA
Note on AN1: AER Ref: DT007/ DT007_a/ DT021/ DT021_a HISTORICAL SERIES (FROM CURRENT BACK 3YRS): Provide maximum seasonal capacity to operate the network (secure, nameplate capacity etc., retirement, downsizing) This specifies the level of support required from non-network service provider. Note: Do not increase accepted capacity if augmentation planned. Unit/Format: MVA
Note on AO1: AER Ref: DT007/ DT007_a/ DT021/ DT021_a HISTORICAL SERIES (FROM CURRENT BACK 3YRS): Provide maximum seasonal capacity to operate the network (secure, nameplate capacity etc., retirement, downsizing) This specifies the level of support required from non-network service provider. Note: Do not increase accepted capacity if augmentation planned. Unit/Format: MVA
Note on AP1: PROJECTED SERIES: Provide maximum seasonal capacity to operate the network (secure, nameplate capacity etc., retirement, downsizing) This specifies the level of support required from non-network service provider. Note: Do not increase accepted capacity if augmentation planned. Unit/Format: MVA
Note on AQ1: PROJECTED SERIES: Provide maximum seasonal capacity to operate the network (secure, nameplate capacity etc., retirement, downsizing) This specifies the level of support required from non-network service provider. Note: Do not increase accepted capacity if augmentation planned. Unit/Format: MVA
Note on AR1: PROJECTED SERIES: Provide maximum seasonal capacity to operate the network (secure, nameplate capacity etc., retirement, downsizing) This specifies the level of support required from non-network service provider. Note: Do not increase accepted capacity if augmentation planned. Unit/Format: MVA
Note on AS1: PROJECTED SERIES: Provide maximum seasonal capacity to operate the network (secure, nameplate capacity etc., retirement, downsizing) This specifies the level of support required from non-network service provider. Note: Do not increase accepted capacity if augmentation planned. Unit/Format: MVA
Note on AT1: PROJECTED SERIES: Provide maximum seasonal capacity to operate the network (secure, nameplate capacity etc., retirement, downsizing) This specifies the level of support required from non-network service provider. Note: Do not increase accepted capacity if augmentation planned. Unit/Format: MVA
Note on AU1: AER Ref: DT008/ DT008_a Provide the POE50 peak load forecast for summer. Unit/Format: MVA
Note on AV1: AER Ref: DT008/ DT008_a Provide the POE50 peak load forecast for summer. Unit/Format: MVA
Note on AW1: AER Ref: DT008/ DT008_a Provide the POE50 peak load forecast for summer. Unit/Format: MVA
Note on AX1: AER Ref: DT008/ DT008_a Provide the POE50 peak load forecast for summer. Unit/Format: MVA
Note on AY1: AER Ref: DT008/ DT008_a Provide the POE50 peak load forecast for summer. Unit/Format: MVA
Note on AZ1: Provide the POE50 peak load forecast for summer. Unit/Format: MVA
Note on BA1: Provide the POE50 peak load forecast for summer. Unit/Format: MVA
Note on BB1: Provide the POE50 peak load forecast for summer. Unit/Format: MVA
Note on BC1: Provide the POE50 peak load forecast for summer. Unit/Format: MVA
Note on BD1: Provide the POE50 peak load forecast for summer. Unit/Format: MVA
Note on BE1: AER Ref: DT008/ DT008_a Provide the POE10 peak load forecast for summer. Unit/Format: MVA
Note on BF1: AER Ref: DT008/ DT008_a Provide the POE10 peak load forecast for summer. Unit/Format: MVA
Note on BG1: AER Ref: DT008/ DT008_a Provide the POE10 peak load forecast for summer. Unit/Format: MVA
Note on BH1: AER Ref: DT008/ DT008_a Provide the POE10 peak load forecast for summer. Unit/Format: MVA
Note on BI1: AER Ref: DT008/ DT008_a Provide the POE10 peak load forecast for summer. Unit/Format: MVA
Note on BJ1: Provide the POE10 peak load forecast for summer. Unit/Format: MVA
Note on BK1: Provide the POE10 peak load forecast for summer. Unit/Format: MVA
Note on BL1: Provide the POE10 peak load forecast for summer. Unit/Format: MVA
Note on BM1: Provide the POE10 peak load forecast for summer. Unit/Format: MVA
Note on BN1: Provide the POE10 peak load forecast for summer. Unit/Format: MVA
Note on BO1: Provide current seasonal nameplate capacity of the network asset. Units/Format: MVA
Note on BP1: Provide the current seasonal secure capacity of the network asset. Note: Some NSPs refer to this as firm capacity. Units/Format: MVA
Note on BQ1: AER Ref: DT007/ DT007_a/ DT021/ DT021_a HISTORICAL SERIES (FROM CURRENT BACK 3YRS): Provide maximum seasonal capacity to operate the network (secure, nameplate capacity etc., retirement, downsizing) This specifies the level of support required from non-network service provider. Note: Do not increase accepted capacity if augmentation planned. Unit/Format: MVA
Note on BR1: AER Ref: DT007/ DT007_a/ DT021/ DT021_a HISTORICAL SERIES (FROM CURRENT BACK 3YRS): Provide maximum seasonal capacity to operate the network (secure, nameplate capacity etc., retirement, downsizing) This specifies the level of support required from non-network service provider. Note: Do not increase accepted capacity if augmentation planned. Unit/Format: MVA
Note on BS1: AER Ref: DT007/ DT007_a/ DT021/ DT021_a HISTORICAL SERIES (FROM CURRENT BACK 3YRS): Provide maximum seasonal capacity to operate the network (secure, nameplate capacity etc., retirement, downsizing) This specifies the level of support required from non-network service provider. Note: Do not increase accepted capacity if augmentation planned. Unit/Format: MVA
Note on BT1: AER Ref: DT007/ DT007_a/ DT021/ DT021_a HISTORICAL SERIES (FROM CURRENT BACK 3YRS): Provide maximum seasonal capacity to operate the network (secure, nameplate capacity etc., retirement, downsizing) This specifies the level of support required from non-network service provider. Note: Do not increase accepted capacity if augmentation planned. Unit/Format: MVA
Note on BU1: AER Ref: DT007/ DT007_a/ DT021/ DT021_a HISTORICAL SERIES (FROM CURRENT BACK 3YRS): Provide maximum seasonal capacity to operate the network (secure, nameplate capacity etc., retirement, downsizing) This specifies the level of support required from non-network service provider. Note: Do not increase accepted capacity if augmentation planned. Unit/Format: MVA
Note on BV1: AER Ref: DT007/ DT007_a/ DT021/ DT021_a HISTORICAL SERIES (FROM CURRENT BACK 3YRS): Provide maximum seasonal capacity to operate the network (secure, nameplate capacity etc., retirement, downsizing) This specifies the level of support required from non-network service provider. Note: Do not increase accepted capacity if augmentation planned. Unit/Format: MVA
Note on BW1: AER Ref: DT007/ DT007_a/ DT021/ DT021_a HISTORICAL SERIES (FROM CURRENT BACK 3YRS): Provide maximum seasonal capacity to operate the network (secure, nameplate capacity etc., retirement, downsizing) This specifies the level of support required from non-network service provider. Note: Do not increase accepted capacity if augmentation planned. Unit/Format: MVA
Note on BX1: AER Ref: DT007/ DT007_a/ DT021/ DT021_a HISTORICAL SERIES (FROM CURRENT BACK 3YRS): Provide maximum seasonal capacity to operate the network (secure, nameplate capacity etc., retirement, downsizing) This specifies the level of support required from non-network service provider. Note: Do not increase accepted capacity if augmentation planned. Unit/Format: MVA
Note on BY1: PROJECTED SERIES: Provide maximum seasonal capacity to operate the network (secure, nameplate capacity etc., retirement, downsizing) This specifies the level of support required from non-network service provider. Note: Do not increase accepted capacity if augmentation planned. Unit/Format: MVA
Note on BZ1: PROJECTED SERIES: Provide maximum seasonal capacity to operate the network (secure, nameplate capacity etc., retirement, downsizing) This specifies the level of support required from non-network service provider. Note: Do not increase accepted capacity if augmentation planned. Unit/Format: MVA
Note on CA1: PROJECTED SERIES: Provide maximum seasonal capacity to operate the network (secure, nameplate capacity etc., retirement, downsizing) This specifies the level of support required from non-network service provider. Note: Do not increase accepted capacity if augmentation planned. Unit/Format: MVA
Note on CB1: PROJECTED SERIES: Provide maximum seasonal capacity to operate the network (secure, nameplate capacity etc., retirement, downsizing) This specifies the level of support required from non-network service provider. Note: Do not increase accepted capacity if augmentation planned. Unit/Format: MVA
Note on CC1: PROJECTED SERIES: Provide maximum seasonal capacity to operate the network (secure, nameplate capacity etc., retirement, downsizing) This specifies the level of support required from non-network service provider. Note: Do not increase accepted capacity if augmentation planned. Unit/Format: MVA
Note on CD1: AER Ref: DT008/ DT008_a Provide the POE50 peak load forecast for winter. Unit/Format: MVA
Note on CE1: AER Ref: DT008/ DT008_a Provide the POE50 peak load forecast for winter. Unit/Format: MVA
Note on CF1: AER Ref: DT008/ DT008_a Provide the POE50 peak load forecast for winter. Unit/Format: MVA
Note on CG1: AER Ref: DT008/ DT008_a Provide the POE50 peak load forecast for winter. Unit/Format: MVA
Note on CH1: AER Ref: DT008/ DT008_a Provide the POE50 peak load forecast for winter. Unit/Format: MVA
Note on CI1: Provide the POE50 peak load forecast for winter. Unit/Format: MVA
Note on CJ1: Provide the POE50 peak load forecast for winter. Unit/Format: MVA
Note on CK1: Provide the POE50 peak load forecast for winter. Unit/Format: MVA
Note on CL1: Provide the POE50 peak load forecast for winter. Unit/Format: MVA
Note on CM1: Provide the POE50 peak load forecast for winter. Unit/Format: MVA
Note on CN1: AER Ref: DT008/ DT008_a Provide the POE10 peak load forecast for winter. Unit/Format: MVA
Note on CO1: AER Ref: DT008/ DT008_a Provide the POE10 peak load forecast for winter. Unit/Format: MVA
Note on CP1: AER Ref: DT008/ DT008_a Provide the POE10 peak load forecast for winter. Unit/Format: MVA
Note on CQ1: AER Ref: DT008/ DT008_a Provide the POE10 peak load forecast for winter. Unit/Format: MVA
Note on CR1: AER Ref: DT008/ DT008_a Provide the POE10 peak load forecast for winter. Unit/Format: MVA
Note on CS1: Provide the POE10 peak load forecast for winter Unit/Format: MVA
Note on CT1: Provide the POE10 peak load forecast for winter Unit/Format: MVA
Note on CU1: Provide the POE10 peak load forecast for winter Unit/Format: MVA
Note on CV1: Provide the POE10 peak load forecast for winter Unit/Format: MVA
Note on CW1: Provide the POE10 peak load forecast for winter Unit/Format: MVA
Note on CX1: Provide Probability of Exceedance (POE) to be used in the NOM calculations. Should be the forecast upon which investment decision is based. Unit/Format: integer (10 or 50)
Note on CY1: AER Ref: DT010 Maximum load at risk Units: MW
Note on CZ1: AER Ref: DT010 Maximum load at risk Units: MW
Note on DA1: AER Ref: DT010 Maximum load at risk Units: MW
Note on DB1: AER Ref: DT010 Maximum load at risk Units: MW
Note on DC1: AER Ref: DT010 Maximum load at risk Units: MW
Note on DD1: AER Ref: DT011 Expected Unserved Energy (EUSE) of the long-term, probability weighted, average energy demanded by customers. Unit/Format: MWh/a
Note on DE1: AER Ref: DT011 Expected Unserved Energy (EUSE) of the long-term, probability weighted, average energy demanded by customers. Unit/Format: MWh/a
Note on DF1: AER Ref: DT011 Expected Unserved Energy (EUSE) of the long-term, probability weighted, average energy demanded by customers. Unit/Format: MWh/a
Note on DG1: AER Ref: DT011 Expected Unserved Energy (EUSE) of the long-term, probability weighted, average energy demanded by customers. Unit/Format: MWh/a
Note on DH1: AER Ref: DT011 Expected Unserved Energy (EUSE) of the long-term, probability weighted, average energy demanded by customers. Unit/Format: MWh/a
Note on DI1: Expected Unserved Energy (EUSE) of the long-term, probability weighted, average energy demanded by customers. Unit/Format: MWh/a
Note on DJ1: Expected Unserved Energy (EUSE) of the long-term, probability weighted, average energy demanded by customers. Unit/Format: MWh/a
Note on DK1: Expected Unserved Energy (EUSE) of the long-term, probability weighted, average energy demanded by customers. Unit/Format: MWh/a
Note on DL1: Expected Unserved Energy (EUSE) of the long-term, probability weighted, average energy demanded by customers. Unit/Format: MWh/a
Note on DM1: Expected Unserved Energy (EUSE) of the long-term, probability weighted, average energy demanded by customers. Unit/Format: MWh/a
Note on DN1: Mandatory: Provide number of hours for which the exceedence forecasted to occur. Unit/Format: h
Note on DO1: Mandatory: Provide number of hours for which the exceedence forecasted to occur. Unit/Format: h
Note on DP1: Mandatory: Provide number of hours for which the exceedence forecasted to occur. Unit/Format: h
Note on DQ1: Mandatory: Provide number of hours for which the exceedence forecasted to occur. Unit/Format: h
Note on DR1: Mandatory: Provide number of hours for which the exceedence forecasted to occur. Unit/Format: h
Note on DS1: Mandatory: Provide number of hours for which the exceedence forecasted to occur. Unit/Format: h
Note on DT1: Mandatory: Provide number of hours for which the exceedence forecasted to occur. Unit/Format: h
Note on DU1: Mandatory: Provide number of hours for which the exceedence forecasted to occur. Unit/Format: h
Note on DV1: Mandatory: Provide number of hours for which the exceedence forecasted to occur. Unit/Format: h
Note on DW1: Mandatory: Provide number of hours for which the exceedence forecasted to occur. Unit/Format: h
Note on DX1: Value of EUSE and is obtained by multiplying the weighted average VCR by the EUSE. Unit/Format: $/a
Note on DY1: Value of EUSE and is obtained by multiplying the weighted average VCR by the EUSE. Unit/Format: $/a
Note on DZ1: Value of EUSE and is obtained by multiplying the weighted average VCR by the EUSE. Unit/Format: $/a
Note on EA1: Value of EUSE and is obtained by multiplying the weighted average VCR by the EUSE. Unit/Format: $/a
Note on EB1: Value of EUSE and is obtained by multiplying the weighted average VCR by the EUSE. Unit/Format: $/a
Note on EC1: Value of EUSE and is obtained by multiplying the weighted average VCR by the EUSE. Unit/Format: $/a
Note on ED1: Value of EUSE and is obtained by multiplying the weighted average VCR by the EUSE. Unit/Format: $/a
Note on EE1: Value of EUSE and is obtained by multiplying the weighted average VCR by the EUSE. Unit/Format: $/a
Note on EF1: Value of EUSE and is obtained by multiplying the weighted average VCR by the EUSE. Unit/Format: $/a
Note on EG1: Value of EUSE and is obtained by multiplying the weighted average VCR by the EUSE. Unit/Format: $/a
Note on EJ1: AER Ref: DT016_a Support Required in Summer. Unit/Format: MW
Note on EK1: AER Ref: DT016 Support Required in Summer. Unit/Format: MVA
Note on EL1: Support Required in Summer. Unit/Format: MVA
Note on EM1: Support Required in Summer. Unit/Format: MVA
Note on EN1: Support Required in Summer. Unit/Format: MVA
Note on EO1: Support Required in Summer. Unit/Format: MVA
Note on EP1: Support Required in Summer. Unit/Format: MVA
Note on EQ1: Support Required in Summer. Unit/Format: MVA
Note on ER1: Support Required in Summer. Unit/Format: MVA
Note on ES1: Support Required in Summer. Unit/Format: MVA
Note on ET1: Support Required in Summer. Unit/Format: MVA
Note on EU1: AER Ref: DT016_a Support Required in Winter. Unit/Format: MW
Note on EV1: AER Ref: DT016 Support Required in Winter. Unit/Format: MVA
Note on EW1: Support Required in winter. Unit/Format: MVA
Note on EX1: Support Required in winter. Unit/Format: MVA
Note on EY1: Support Required in winter. Unit/Format: MVA
Note on EZ1: Support Required in winter. Unit/Format: MVA
Note on FA1: Support Required in winter. Unit/Format: MVA
Note on FB1: Support Required in winter. Unit/Format: MVA
Note on FC1: Support Required in winter. Unit/Format: MVA
Note on FD1: Support Required in winter. Unit/Format: MVA
Note on FE1: Support Required in winter. Unit/Format: MVA
Note on FF1: Supports solution for AER Refs: DT007_a, DT008_a, DT017_a, DT021_a Asset specific power factor Format: Decimal between 0 and 1
Note on FG1: Optional: Description of reactive power requirements in an area. Unit/Format: Free text
Note on FH1: AER Ref: DT017/ DT017_a
Note on FI1: AER Ref: DT018 Emergency generation capacity available within constrained area Format: MVA
Note on FJ1: AER Ref: DT018_a Emergency generation capacity available within constrained area Format: MW
Note on FK1: AER Ref: DT019/ DT019_a Format: 'Yes' or 'No' Assets marked Yes will have 3yr half hourly data supplied in AER_NOM_emergencyresponse_data.xlsx and those with No will not.
Note on FL1: Mandatory: Provide the codenames of the Distribution Zone Substations (ZS) that are connected to the network asset. Note: ZS connections are only required to be entered for STL, TS and TL assets. Unit/Format: Free text.
Note on FM1: Optional: Enter Effectiveness Factor associated with demand management undertaken in each downstream ZS area. If left blank a default of 100% will be used. Unit/Format: %
Note on FN1: Mandatory: Provide the codenames of the Distribution Zone Substations (ZS) that are connected to the network asset. Note: ZS connections are only required to be entered for STL, TS and TL assets. Unit/Format: Free text.
Note on FO1: Optional: Enter Effectiveness Factor associated with demand management undertaken in each downstream ZS area. If left blank a default of 100% will be used. Unit/Format: %
Note on FP1: Mandatory: Provide the codenames of the Distribution Zone Substations (ZS) that are connected to the network asset. Note: ZS connections are only required to be entered for STL, TS and TL assets. Unit/Format: Free text.
Note on FQ1: Optional: Enter Effectiveness Factor associated with demand management undertaken in each downstream ZS area. If left blank a default of 100% will be used. Unit/Format: %
Note on FR1: Mandatory: Provide the codenames of the Distribution Zone Substations (ZS) that are connected to the network asset. Note: ZS connections are only required to be entered for STL, TS and TL assets. Unit/Format: Free text.
Note on FS1: Optional: Enter Effectiveness Factor associated with demand management undertaken in each downstream ZS area. If left blank a default of 100% will be used. Unit/Format: %
Note on FT1: Mandatory: Provide the codenames of the Distribution Zone Substations (ZS) that are connected to the network asset. Note: ZS connections are only required to be entered for STL, TS and TL assets. Unit/Format: Free text.
Note on FU1: Optional: Enter Effectiveness Factor associated with demand management undertaken in each downstream ZS area. If left blank a default of 100% will be used. Unit/Format: %
Note on FV1: Mandatory: Provide the codenames of the Distribution Zone Substations (ZS) that are connected to the network asset. Note: ZS connections are only required to be entered for STL, TS and TL assets. Unit/Format: Free text.
Note on FW1: Optional: Enter Effectiveness Factor associated with demand management undertaken in each downstream ZS area. If left blank a default of 100% will be used. Unit/Format: %
Note on FX1: Mandatory: Provide the codenames of the Distribution Zone Substations (ZS) that are connected to the network asset. Note: ZS connections are only required to be entered for STL, TS and TL assets. Unit/Format: Free text.
Note on FY1: Optional: Enter Effectiveness Factor associated with demand management undertaken in each downstream ZS area. If left blank a default of 100% will be used. Unit/Format: %
Note on FZ1: Mandatory: Provide the codenames of the Distribution Zone Substations (ZS) that are connected to the network asset. Note: ZS connections are only required to be entered for STL, TS and TL assets. Unit/Format: Free text.
Note on GA1: Optional: Enter Effectiveness Factor associated with demand management undertaken in each downstream ZS area. If left blank a default of 100% will be used. Unit/Format: %
Note on GB1: Mandatory: Provide the codenames of the Distribution Zone Substations (ZS) that are connected to the network asset. Note: ZS connections are only required to be entered for STL, TS and TL assets. Unit/Format: Free text.
Note on GC1: Optional: Enter Effectiveness Factor associated with demand management undertaken in each downstream ZS area. If left blank a default of 100% will be used. Unit/Format: %
Note on GD1: Mandatory: Provide the codenames of the Distribution Zone Substations (ZS) that are connected to the network asset. Note: ZS connections are only required to be entered for STL, TS and TL assets. Unit/Format: Free text.
Note on GE1: Optional: Enter Effectiveness Factor associated with demand management undertaken in each downstream ZS area. If left blank a default of 100% will be used. Unit/Format: %
Note on GF1: Mandatory: Provide the codenames of the Distribution Zone Substations (ZS) that are connected to the network asset. Note: ZS connections are only required to be entered for STL, TS and TL assets. Unit/Format: Free text.
Note on GG1: Optional: Enter Effectiveness Factor associated with demand management undertaken in each downstream ZS area. If left blank a default of 100% will be used. Unit/Format: %
Note on GH1: Mandatory: Provide the codenames of the Distribution Zone Substations (ZS) that are connected to the network asset. Note: ZS connections are only required to be entered for STL, TS and TL assets. Unit/Format: Free text.
Note on GI1: Optional: Enter Effectiveness Factor associated with demand management undertaken in each downstream ZS area. If left blank a default of 100% will be used. Unit/Format: %
Note on GJ1: Mandatory: Provide the codenames of the Distribution Zone Substations (ZS) that are connected to the network asset. Note: ZS connections are only required to be entered for STL, TS and TL assets. Unit/Format: Free text.
Note on GK1: Optional: Enter Effectiveness Factor associated with demand management undertaken in each downstream ZS area. If left blank a default of 100% will be used. Unit/Format: %
Note on GL1: Mandatory: Provide the codenames of the Distribution Zone Substations (ZS) that are connected to the network asset. Note: ZS connections are only required to be entered for STL, TS and TL assets. Unit/Format: Free text.
Note on GM1: Optional: Enter Effectiveness Factor associated with demand management undertaken in each downstream ZS area. If left blank a default of 100% will be used. Unit/Format: %
Note on GN1: Mandatory: Provide the codenames of the Distribution Zone Substations (ZS) that are connected to the network asset. Note: ZS connections are only required to be entered for STL, TS and TL assets. Unit/Format: Free text.
Note on GO1: Optional: Enter Effectiveness Factor associated with demand management undertaken in each downstream ZS area. If left blank a default of 100% will be used. Unit/Format: %
Note on GP1: Mandatory: Provide the codenames of the Distribution Zone Substations (ZS) that are connected to the network asset. Note: ZS connections are only required to be entered for STL, TS and TL assets. Unit/Format: Free text.
Note on GQ1: Optional: Enter Effectiveness Factor associated with demand management undertaken in each downstream ZS area. If left blank a default of 100% will be used. Unit/Format: %
Note on GR1: Mandatory: Provide the codenames of the Distribution Zone Substations (ZS) that are connected to the network asset. Note: ZS connections are only required to be entered for STL, TS and TL assets. Unit/Format: Free text.
Note on GS1: Optional: Enter Effectiveness Factor associated with demand management undertaken in each downstream ZS area. If left blank a default of 100% will be used. Unit/Format: %
Note on GT1: Mandatory: Provide the codenames of the Distribution Zone Substations (ZS) that are connected to the network asset. Note: ZS connections are only required to be entered for STL, TS and TL assets. Unit/Format: Free text.
Note on GU1: Optional: Enter Effectiveness Factor associated with demand management undertaken in each downstream ZS area. If left blank a default of 100% will be used. Unit/Format: %
Note on GV1: Mandatory: Provide the codenames of the Distribution Zone Substations (ZS) that are connected to the network asset. Note: ZS connections are only required to be entered for STL, TS and TL assets. Unit/Format: Free text.
Note on GW1: Optional: Enter Effectiveness Factor associated with demand management undertaken in each downstream ZS area. If left blank a default of 100% will be used. Unit/Format: %
Note on GX1: Mandatory: Provide the codenames of the Distribution Zone Substations (ZS) that are connected to the network asset. Note: ZS connections are only required to be entered for STL, TS and TL assets. Unit/Format: Free text.
Note on GY1: Optional: Enter Effectiveness Factor associated with demand management undertaken in each downstream ZS area. If left blank a default of 100% will be used. Unit/Format: %
Note on GZ1: Mandatory: Provide the codenames of the Distribution Zone Substations (ZS) that are connected to the network asset. Note: ZS connections are only required to be entered for STL, TS and TL assets. Unit/Format: Free text.
Note on HA1: Optional: Enter Effectiveness Factor associated with demand management undertaken in each downstream ZS area. If left blank a default of 100% will be used. Unit/Format: %
Note on HB1: Mandatory: Provide the codenames of the Distribution Zone Substations (ZS) that are connected to the network asset. Note: ZS connections are only required to be entered for STL, TS and TL assets. Unit/Format: Free text.
Note on HC1: Optional: Enter Effectiveness Factor associated with demand management undertaken in each downstream ZS area. If left blank a default of 100% will be used. Unit/Format: %
Note on HD1: Mandatory: Provide the codenames of the Distribution Zone Substations (ZS) that are connected to the network asset. Note: ZS connections are only required to be entered for STL, TS and TL assets. Unit/Format: Free text.
Note on HE1: Optional: Enter Effectiveness Factor associated with demand management undertaken in each downstream ZS area. If left blank a default of 100% will be used. Unit/Format: %
Note on HF1: Mandatory: Provide the codenames of the Distribution Zone Substations (ZS) that are connected to the network asset. Note: ZS connections are only required to be entered for STL, TS and TL assets. Unit/Format: Free text.
Note on HG1: Optional: Enter Effectiveness Factor associated with demand management undertaken in each downstream ZS area. If left blank a default of 100% will be used. Unit/Format: %
Note on HH1: Mandatory: Provide the codenames of the Distribution Zone Substations (ZS) that are connected to the network asset. Note: ZS connections are only required to be entered for STL, TS and TL assets. Unit/Format: Free text.
Note on HI1: Optional: Enter Effectiveness Factor associated with demand management undertaken in each downstream ZS area. If left blank a default of 100% will be used. Unit/Format: %
Note on HJ1: Mandatory: Provide the codenames of the Distribution Zone Substations (ZS) that are connected to the network asset. Note: ZS connections are only required to be entered for STL, TS and TL assets. Unit/Format: Free text.
Note on HK1: Optional: Enter Effectiveness Factor associated with demand management undertaken in each downstream ZS area. If left blank a default of 100% will be used. Unit/Format: %
Note on HL1: Mandatory: Provide the codenames of the Distribution Zone Substations (ZS) that are connected to the network asset. Note: ZS connections are only required to be entered for STL, TS and TL assets. Unit/Format: Free text.
Note on HM1: Optional: Enter Effectiveness Factor associated with demand management undertaken in each downstream ZS area. If left blank a default of 100% will be used. Unit/Format: %
Note on HN1: Mandatory: Provide the codenames of the Distribution Zone Substations (ZS) that are connected to the network asset. Note: ZS connections are only required to be entered for STL, TS and TL assets. Unit/Format: Free text.
Note on HO1: Optional: Enter Effectiveness Factor associated with demand management undertaken in each downstream ZS area. If left blank a default of 100% will be used. Unit/Format: %
Note on HP1: Mandatory: Provide the codenames of the Distribution Zone Substations (ZS) that are connected to the network asset. Note: ZS connections are only required to be entered for STL, TS and TL assets. Unit/Format: Free text.
Note on HQ1: Optional: Enter Effectiveness Factor associated with demand management undertaken in each downstream ZS area. If left blank a default of 100% will be used. Unit/Format: %
Note on HR1: Mandatory: Provide the codenames of the Distribution Zone Substations (ZS) that are connected to the network asset. Note: ZS connections are only required to be entered for STL, TS and TL assets. Unit/Format: Free text.
Note on HS1: Optional: Enter Effectiveness Factor associated with demand management undertaken in each downstream ZS area. If left blank a default of 100% will be used. Unit/Format: %